## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0007 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1656 |  |  | Transmital Date: 12/6/2022
Document Title: P&ID - 1st Stage Gas Compression Compressors |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1656 |  |  | Transmital Date: 12/6/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PI-0007_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نقطه نظر پیشین: نهايي سازي خطوط فلر منوط به تایید محاسبات مربوطه می باشد. |  | BK-SUR-ENG-PCS-01-06467 | 2022-12-21 | پس از نهایی شدن محاسبات فلر مدرک فوق نیز بروز رسانی خواهد شد.
2 | نقطه نظر پیشین: نهايي سازي اين دياگرام، منوط به دريافت دياگرام سازنده مي باشد. |  | BK-SUR-ENG-PCS-01-06467 | 2022-12-21 | پس از دریافت اطلاعات از سازنده، اصلاحات لازم در مطالعات AS BUILT صورت می گیرد.
3 | برای اعمال HAZOP Recommendation شماره 44، می بایست از XV به ESDV، استفاده گردد. |  | BK-SUR-ENG-PCS-01-06467 | 2022-12-21 | از آنجا که شیر فوق از هر دو سیستم کنترلی و اضطراری دستور گرفته و نیز با فعال شدن سطح ESD-2A در فرآیند DEPRESSURIZING قرار می گیرد. لذا شیر فوق با تگ BDV نمایش داده شده و توضیحات لازم به صورت NOTE (NOTE-17) در نقشه لحاظ گردیده است.
4 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-01-06467 | 2022-12-21 | اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: