## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0014 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1657 |  |  | Transmital Date: 12/6/2022
Document Title: P&ID - Lean Glycol Storage Tank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1657 |  |  | Transmital Date: 12/6/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PI-0014_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Strainer به صورت فلنجی نمایش داده شود. |  | BK-SUR-ENG-PCS-01-06508 | 2022-12-24 | اعمال گردید.
2 | سایز کلیه شیرها و همچنین میزان شیب خطوط، در نقشه نمایش داده شود. |  | BK-SUR-ENG-PCS-01-06508 | 2022-12-24 | در ویرایش قبلی نمایش داده شده است.
3 | برای تمامی شیرهای با سایز کم تر از 2 اینچ، Blind ها به صورت Cap نمایش داده شود. |  | BK-SUR-ENG-PCS-01-06508 | 2022-12-24 | اعمال گردید.
4 | نقطه نظر پیشین: Remote Start برای پمپهای 2103، مجاز نمی باشد. |  | BK-SUR-ENG-PCS-01-06508 | 2022-12-24 | کلیه تصمیم گیری ها در خصوص فرمان remote start بر مبنای جلسات Hazop/Hazid صورت گرفته است. لذا امکان اعمال تغییرات مذکور فراهم نمی باشد.
5 | نقطه نظر پیشین: برای Safety Hatch می بایست نازل جدا در نظر گرفته شود. |  | BK-SUR-ENG-PCS-01-06508 | 2022-12-24 | اعمال گردید.
6 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-01-06508 | 2022-12-24 | اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: