## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0015 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1657 |  |  | Transmital Date: 12/6/2022
Document Title: P&ID - Instrument & Plant Air System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1657 |  |  | Transmital Date: 12/6/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0015_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پیرو نظرات پیشین این امور در بند اول نامه 1401/2294/283491(1401/08/07) تله مکانیکی برای Wet Air K.O.D در نظر گرفته شود. |  | 1401-2294-448441 | 1401/11/30 | Wet K.O.D در پکیج قرار دارد و سازنده پکیج آن را لحاظ خواهد کرد.لازم به ذکر است نمایش تجهیزات داخل پکیج سازنده پس از دریافت اطلاعات سازندگان در ویرایش As Built نمایش داده خواهد شد.
2 | پیرو نظرات پیشین این امور در بند اول نامه 1401/2294/415389(1401/11/01) بروی مدرک "Relief Load Summary"برای شیر PSV-2201 می باید شیر یدک خریداری شده و تحویل کارفرما شود. لازم نیست در مدرک P&ID نشان داده شود. |  | 1401-2294-448441 | 1401/11/30 | پیرو نظرات کارفرمای محترم در بند اول نامه 1401/2294/415389(1401/11/01) بروی مدرک "Relief Load Summary"برای شیر PSV-2201 ، شیر یدک خریداری شددر نظر گرفته شده است و Note مربوطه در مدرک اعمال گردید.
3 | دلیل تغییر Failure Mode شیر PCV-2201 از FC به FO چیست. |  | 1401-2294-448441 | 1401/11/30 | مطابق بند 82 مطالعات HAZOP اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: