## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-PR-LI-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1415 |  |  | Transmital Date: 9/19/2022
Document Title: Consumption List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1415 |  |  | Transmital Date: 9/19/2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-PR-LI-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در مدرك براي محاسبه ميزان هواي ابزار دقيق مورد نياز به عمل نمودن 30 % از On/Off Valve ها همزمان با عملكرد كليه شيرهاي كنترلي اشاره شده است، در حالیکه در محاسبات ایستگاه تقویت فشار گاز، مبانی دیگری در نظر گرفته شده است که می بایست این مبانی در بخشهای مختلف پروژه یکسان سازی گردد. |  | BK-SUR-ENG-PCS-01-05873 | 2022-10-10 | فلسفه کنترل در منیفولد و ایستگاه تقویت فشار متفاوت می باشد. در منیفولد در یک خط لوله جریانی شیر On/Off و شیر کنترلی همزمانی نخواهد داشت ولی زمانی که یک خط لوله جریانی shut down می شود سایر خطوط جریانی می تواند در مدار باشند. در مدرک فوق فرض شده است زمانی که دو خط لوله جریانی shutdown می شود 4 خط دیگر در سرویس است. لازم به ذکر است که ستاریو فوق حداکثر میزان هوای ابزار دقیق را محاسبه می نماید.
2 | لازم است نقطه نظرات ذينفع اصلي اعمال گردد. |  | BK-SUR-ENG-PCS-01-05873 | 2022-10-10 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021