## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-PY-0004_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1777 |  |  | Transmital Date: 08-Jan-2023
Document Title: Earthing & Lightning Layout - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-EL-TR-1777 |  |  | Transmital Date: 08-Jan-2023
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-PY-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اینکه در این واحد توسعه فنس و خطوط لوله نیز در دستور کار می باشد، ضروری است جزئیات مربوط به اتصال ارت به فنس و خطوط لوله نیز ارائه گرد. |  | 1401-2294-444077 | 1401-11-19 | با توجه به اینکه در مدرک محاسبات ارتینگ، جدول مربوط به ارت فنس آورده شده است، لذا به یک نوت اکتفاد شده است. لذا خواهشمند است نوت شماره 5 ملاحظه گردد.
2 | کلیه چاههای ارت همبندی و به شبکه ارت موجود وصل گردند. |  | 1401-2294-444077 | 1401-11-19 | اعمال گردید.
3 | بدنه فلزی تابلوهای UPS و شارژر از دو نقطه ارت گردند. |  | 1401-2294-444077 | 1401-11-19 | اعمال گردید.
4 | نگهدارنده باتری سیستم نیز می بایست از دو نقطه ارت گردد. |  | 1401-2294-444077 | 1401-11-19 | اعمال گردید.
5 | ارت بدنه سوییچ باکس های باتری در مدرک نمایش داده شوند. |  | 1401-2294-444077 | 1401-11-19 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadataian | Signature |  |  |  | Clarified By: | Signature
| Date: 21-Jan-23 |  |  |  |  | Date: