## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-PY-0004_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1777 |  |  | Transmital Date: 08-Jan-2023
Document Title: Earthing & Lightning Layout - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-EL-TR-1777 |  |  | Transmital Date: 08-Jan-2023
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-EL-PY-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised as AFC after finalizing or minor comments on "Calculation Note for DC Charger System - Extension of Binak B/C Manifold" and "Electrical Equipment Arrangement Layout In Building - Extension of Binak B/C Manifold" document. |  | BK-SUR-ENG-ELE-01-06708 | 2023-01-21 | در صورت ایجاد هرگونه تغییر در مدارک مشابه، این مدرک به روزرسانی خواهد شد.
2 | Fuse box shall be shown and connected to earth bar. |  | BK-SUR-ENG-ELE-01-06708 | 2023-01-21 | اعمال گردید.
3 | The AC/DC UPS panel and battery rack shall be connected to earth bar from two side. |  | BK-SUR-ENG-ELE-01-06708 | 2023-01-21 | اعمال گردید.
4 | Description for rod (Such as 0.019mm2 and test well) shall be modified in legend. Meanwhile earth bar shall be with base plate and isolators. |  | BK-SUR-ENG-ELE-01-06708 | 2023-01-21 | اصلاح گردید. همچنین توضیحات تکمیلی در MTO آورده خواهد شد.
5 | Regarding to the existing LV switchgear has been connected to existing earthing system so there is not require to earth again and the shown earthing system can be deleted. |  | BK-SUR-ENG-ELE-01-06708 | 2023-01-21 | اعمال گردید.
6 | earthing conductor shall be connected to existing earth bars in all rooms. New earth bars will be installed only in case of lack of earth bar in that room. This item shall be added as a note. |  | BK-SUR-ENG-ELE-01-06708 | 2023-01-21 | نوت اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 21-Jan-23 |  |  |  |  | Date: