## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1798 |  |  | Transmital Date: 16-Jan-2023
Document Title: Area Electrical Cable Route & Section Layout - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-EL-TR-1798 |  |  | Transmital Date: 16-Jan-2023
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در محل عبور کابل از جاده، ترانشه کابل بصورت کاندوییت بانک می بایست اجرا و در مدرک نمایش داده شود. |  | 1401-2294-448439 | 1401-11-24 | اعمال گردید.
2 | در محوطه زیر پایپ رک، کابل بصورت دفنی اجرا شود. |  | 1401-2294-448439 | 1401-11-24 | با توجه به اینکه امکان دسترسی به زیر پایپ رک موجود وجود ندارد، در بخش برق و ابزاردقیق تا نزدیکی پایپ رک از ترنچ خاکی استفاده شده است، و جهت عبور از پایپ رک از سینی و لدر استفاده شده و در انتها و جهت عبور از جاده داکت بانک نصب خواهد شد.
3 | جزئیات مربوط به تقاطع ترانشه کابل با ترانشه های موجود، ارائه گردد. |  | 1401-2294-448439 | 1401-11-24 | با توجه به اینکه جزئیات نقشه های موجود در اختیار این مشاور نمی باشد، لذا بر اساس برداشت اطلاعاتی که مهندسین این مشاور از ترنچهای موجود در بخش ابزاردقیق انجام داده اند، سعی می گردد از همین ترنچها جهت انتقال کابلها استفاده گردد. در قسمت انتهایی که مربوط به برقرسانی به موتور سمت پایپ رک می باشد، نیز سینی و لدر و داکت بانک جدید استفاده خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 25-Jan-23 |  |  |  |  | Date: