## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
SET POINT & ALARM LIST-WELLHEADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | IN | LI | 0002 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
SET POINT & ALARM LIST-WELLHEADS نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | APR.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.mehrshad
D00 |  | SEP.2021 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number:F0Z-709420
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
SET POINT & ALARM LIST-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 | IN | LI | 0002 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | X | [7 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
SET POINT & ALARM LIST-WELLHEADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از 7
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 000 | IN | LI | 0002 | D01
REFERENCE DOCUMENTS:
1- PIPING & INSTRUMENT DIAGRAM:
| P&ID - W018S | [8 empty] | BK-W018S-PEDCO-110-PR-PI-0001
| P&ID - W028 | [8 empty] | BK-W028-PEDCO-110-PR-PI-0001
| P&ID - W035 | [8 empty] | BK-W035-PEDCO-110-PR-PI-0001
| P&ID - W008N | [8 empty] | BK-W008N-PEDCO-110-PR-PI-0001
2- SPECIFICATION FOR WHCP/HPU | [9 empty] | BK-SSGRL-PEDCO-110-IN-SP-0001
3- WHCP HYDRAULIC/PNEUMATIC DIAGRAM- WELLHEADS | [9 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002

## 018S
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
SET POINT & ALARM LIST-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 |  | IN | LI |  | 0002 | D01
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1101A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1101A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200
TAG NO. | PSHH-1101B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 242 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1101B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 242 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200

## 008N
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
SET POINT & ALARM LIST-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 |  | IN | LI |  | 0002 | D01
PRESSURE SENSING LINE/ SWITCHES FOR WELL NO.008N
TAG NO. | PSHH-1601A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1601A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200
TAG NO. | PSHH-1601B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 230 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1601B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  | 75 | [5 empty] | 1/2" |  | CRUDE OIL | 230 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  | 100 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200

## 028
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
SET POINT & ALARM LIST-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 |  | IN | LI |  | 0002 | D01
PRESSURE SENSING LINE/ SWITCHES FOR WELL NO. W028
TAG NO. | PSHH-1401A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1401A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200
TAG NO. | PSHH-1401B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 273 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1401B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 273 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200

## 035
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
SET POINT & ALARM LIST-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 |  | IN | LI |  | 0002 | D01
PRESSURE SENSING LINE / SWITCHES FOR WELL NO. W035
TAG NO. | PSHH-1501A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1501A | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200
TAG NO. | PSHH-1501B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 298 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1501B | P&IDs No. |  |  | OPER. TEMP. (°C) |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  | 80 | [5 empty] | 1/2" |  | CRUDE OIL | 298 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  | DSG. TEMP. (°C) |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  | 105 | [5 empty] | BY VENDOR |  | SS 316 | 5000 | 200