## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR DC CHARGER OF WELL PADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | EL | DT | 0003 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR DC CHARGER OF WELL PADS نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | Apr.2023 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | Apr.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | Mar.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Jan.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-707390
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR DC CHARGER OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 110 | EL | DT | 0003 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 51
2 | X | X | X |  | X |  |  |  | 52
3 | X | X | X | [5 empty] | 53
4 | X | X | X | [5 empty] | 54
5 | X | X | X | [5 empty] | 55
6 | X | X | X | [5 empty] | 56
7 | X | X | X | [5 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## 110 VDC.
Technical Data For Industrial Battery & Battery Charger for 110 VDC of Wellpads
Item | Description | Required | Vendor Data
1-General
1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
1.2 | Manufacturer | By Vendor
1.3 | Manufacturer Model | By Vendor
1.4 | Average Ambient Temperature (Min/Max) | Min ~ Max: -5 ~ +52°C
1.5 | Max.Design Temperature: | 52 °c
1.6 | Max. Sun Temperature: | + 85 °c
1.7 | Max.Relative Humidity: | 100%
1.8 | Mean Sea Level: | 12.5 m above Sea Level
1.9 | Seismic Factor: | 0.3g
1.10 | Max. Wind Velocity(Max) | 120 km/hr
1.11 | Standard(s) | IEC,IPS-M-EL-174(2), IPS-E-EL-100(1)
1.12 | Quantity | 6 Complete set (2×100% Charger) with commissioning and two years Spare Parts, Two battery bank(2×92cell), Battery Stand with special tools for Batteries, switch-fuse For Battery Banks: Exd IIC-T3 type.
1.13 | Service | 110 VDC for LV Switchgear
1.14 | Tag Number | WellXX-110-CHG-001 & WellXX-110-CHG-002
1.15 | Applicable SLD | BK-SSGRL-PEDCO-110-EL-SL-0002
1.16 | Applicable Specification | BK-GNRAL-PEDCO-000-EL-SP-0005
1.17 | Location | Indoor
2-Environment
2.1 | Area classification | Safe Area
2.2 | Site Elevation | 12.5 m
2.3 | Ambient Temperature | Min/Max: -5/52°C
2.4 | Relative humidity | 100%
2.5 | Atmosphere | Tropical & Dusty
2.6 | Building Temperature Control | Not Required
2.7 | Seismic Acceleration | 0.3g
3.AC Input
3.1 | Rectifiers Input Voltage | 380/400/440, 3Ph, Cable 4 Core, 50 Hz
3.2 | Max.allowable input voltage variation | ±10%
3.3 | Max.allowable input frequency variation | ±5%
3.4 | Network short circuit current (rms) | 50KA
3.5 | Network short circuit current (Peak) | By Vendor
3.6 | Max. short circuit clearing time | 1 sec
3.7 | Max. power consumption | By Vendor
3.8 | Input THDi% ( acc to IEEE-519 ) | <10%
4.DC Output
4.1 | Rated voltage | 110 VDC
4.2 | Max. Allowable Voltage Variation | ±1%
4.3 | Rated Output Current (Amp) | 14.68 Amp
4.4 | Allowable Ripple voltage (r.m.s ) | <1%
4.6 | Rectifier control voltage (Full Control) | 12 Pulse
4.7 | Charger Topology | Hot Duty Standby
4.8 | Rectifier Input Filter type | R.F.I & Surge Arrester
4.9 | Constant Voltage Control | Required
4.10 | Constant Current Control | Required
4.11 | Rectifier Over Load (%) | 110% Continues
4.12 | Rectifiers Protection | Required
4.13 | MCCB for AC Inputs | Required
4.14 | MCCB for DC Output | Required
4.15 | Ultra Fast Fuse to Protect Thrusters | Required
4.16 | Charger Output Fuse | Required
4.17 | AC Input Voltmeter | Required
4.18 | AC Input Ammeter | Required
4.19 | Charger DC Voltmeter | Required
4.20 | Charger DC Ammeter | Required
4.21 | Charger DC LC Filter | Required
4.22 | Load Current Ammeter | Required
4.23 | Charger Selector Switch | Required
4.24 | Battery Low DC Alarm (Indicator & Dry Contact) | Required
4.25 | Load Low DC Alarm (Indicator & Dry Contact) | Required
4.26 | Load Hi DC Alarm (Indicator & Dry Contact) | Required
4.27 | Batteries Disconnected (Indicator) | Required
5.Battery Charger Cabinet
5.1 | Type | Flat Face
5.2 | Construction | Floor Mounted, Free Standing
5.3 | Ingress protection class | IP42
5.4 | Access for maintenance | Front
5.5 | Body material | Carbon Steel Sheet
5.6 | Thickness of body material | Min.2 mm
5.7 | Finish color | RAL 7032
5.8 | Cable entrance | Bottom and Cable Gland
5.9 | Bottom closing method | By Vendor
5.10 | Cooling method | Natural
5.11 | Space Heater | Required
5.12 | Illumination | Required
5.13 | Noise level | 70dBA
5.14 | Wiring | Power and Control Min.2.5mm², Metering Min.1.5mm²
5.15 | Nameplate | English Black in White Background
5.16 | Earthling System | IT
Note1: Data shown are typical; manufacturer shall provide his own data
Note2: The blank items shall be filled by battery manufacture
6.Batteries
6.1 | Manufacturer | SAFT
6.2 | Manufacturer Model | By Vendor
6.3 | Standard | IEC 60623, IEEE 1115 2014
6.4 | Quantity | 1 Complete set (2×50% Battery Bank)
6.5 | Service | 110 VDC for LV Switchgear
6.6 | Applicable Specification | BK-GNRAL-PEDCO-000-EL-SP-0005
6.7 | Location | Indoor
6.8 | Battery requirements | By Vendor
6.9 | Battery type | Nickel-Cadmium (IEC60623)
6.10 | Battery charging method | Constant Voltage-Dual Rate and Current Limit with Float/Auto/Equalize/Initial Mode charging
6.11 | Back-up time | 8 Hr
6.12 | Emergency Mode Voltage for each cell (Activated by Battery Room Fan Failure) | 1.35 V ± 0.01 V
6.13 | Battery float charging voltage | 1.4~1.45 V/Cell
6.14 | Battery Equalize charging voltage ( 0-30Hr Timer and Reset Push Button are required) | 1.45~1.55 V/Cell
6.15 | Battery boost charging voltage ( 0-30Hr Timer and Reset Push Button are required) | 1.55~1.65 V/Cell
6.16 | Battery initial charging voltage ( 0-30Hr Timer and Returnable Switch are required) | 1.75 V/Cell
6.17 | Battery nominal voltage | 1.2 V/Cell
6.18 | Final discharge voltage per cell(V) | 1.14 V/Cell
6.19 | Rated capacity of each cell at 20 ⁰C | Min 30 Ah
6.2 | Re-charging time to 90% Rated Capacity | 8 Hours
6.21 | Required battery ampere-hour (C5) | 30Ah , SBLE Type
6.22 | Total quantity of cells | 184
6.23 | No. of battery banks | 2
6.24 | No. of batteries per each bank | 92
6.25 | Battery cell dimension (W × D × H ) | By Vendor
6.26 | Battery cell weight | By Vendor
6.27 | Batteries shall be performed from SAFT,ALCAD Batteries | Required
6.28 | All type of Batteries and Battery accessories shall be original and approved by Iranian representative | Required
6.29 | Rate of H2 production during charging | Liter/Cell
6.3 | Required air volume of exchange in battery room | m3/Hours
6.31 | Required air volume of electrolyte | By Vendor
6.32 | Composition of electrolyte | By Vendor
6.33 | Required volume of electrolyte | Liter
6.34 | Required Max. charging current | By Vendor
7.Data sheet for Battery
7.1 | Battery Discharging Rate | Long Rate
7.2 | Container | Plastic
7.3 | Construction | Vented
8.Accessories & Special Tools
8.1 | Thermometer | Required
8.2 | Hydrometer | Required
8.3 | Voltmeter | Required
8.4 | Battery Racks | Required (Seismic Factor:0.3g)
8.5 | Flame Arrester | Required
8.6 | Stand Type | By Vendor
9.Load Profile Graph
9.1 | T1 :1 Min
9.2 | I1 :507 W
9.3 | T2 : 7Hr , 58 Min
9.4 | I2 : 147 W
9.5 | T3 : 1 Min
9.6 | I3 : 507 W
10.Data Sheet for Distribution Board
10.1 | Standard | IEC,IPS-M-EL-174(2), IPS-E-EL-100(1)
10.2 | Quantity | 1 Complete set
10.3 | Service | DC Distribution Panel
11.Mechanical specification
11.1 | Mounting type | Floor Mounted, Free Standing
11.2 | Body martial | Carbon Steel Sheet
11.3 | Thickness | Min.2 mm
11.4 | Access for maintenance | Front
11.5 | Protection class | IP42
11.6 | Illumination | Required
11.7 | Space heater | Required
11.8 | Weight | By Vendor
11.9 | Dimensions | By Vendor
11.10 | Name plate | English Black in White Background
11.12 | Finished color | RAL 7032
12.Electrical Specification
12.1 | Rated incoming voltage | 110 VDC
12.2 | Rated insulation voltage | By Vendor
12.3 | Wiring | Power and Control Min.2.5mm²,Metering Min.1.5mm²,
13.Incoming
13.1 | Incoming Cables Size & Tag no. | BK-GCS-PEDCO-120-EL-SL-0006
13.2 | Entry Side | Bottom by Cable Gland
13.3 | Cable Entry | Via Removable Gland Plate
13.4 | Incoming Circuit breaker | MCCB
14.3 | Terminal Type and quantity | By Vendor
13.5 | Circuit breaker construction | Fix
14.Outgoing
14.1 | Outgoing cable size and tag no. | BK-SSGRL-PEDCO-110-EL-CN-0005
14.2 | Entry side | Bottom by Cable Gland
15.Data Sheet for Distribution Board
15.1 | Cable entry | Via Removable Gland Plate
15.2 | Outgoing circuit breaker | MCB
15.3 | Circuit breaker constructor | Fix
16.Indicating lights , Alarms and Accessories
16.1 | Battery Low DC alarm | Required ,With Dry Contacts
16.2 | Load Low DC alarm | Required ,With Dry Contacts
16.3 | Load Hi DC alarm | Required ,With Dry Contacts
16.4 | Batteries disconnected | Required
16.5 | Battery voltmeter | Required
16.6 | Battery ammeter | Required
16.7 | Load voltmeter | Required
16.8 | Load ammeter | Required
16.9 | Cable gland | Required
16.10 | Removable gland plate | Required
17.Tests ( Factory Acceptance test and Site Acceptance Test shall be performed By the Vendor )
17.1 | Visual Inspection & Dimensional Check | Required
17.2 | Performance and Function Test | Required
17.3 | Sequence , Operation and Logic Test | Required
17.4 | Dielectric Strength Test | Required
17.5 | Output Voltage and Ripple Check | Required
17.6 | Charger Voltage Adjustment Test | Required
17.7 | THDi% Check | Required
17.8 | Output Regulation / Adjustments Test | Required
17.9 | Alarms Check | Required
17.10 | Autonomy Test | Required
17.11 | Current Limit Test | Required
17.12 | Short Circuit test | Required
17.13 | Other Tests shall be performed in Accordance with IEC60146 (Battery Charger Testing) | Required
17.14 | Hardware and Software for Communication, Programming or Setting up the CPU or MPU Boards (If Required), | Required
18.Accessories And Special Tools
18.1 | MIMIC Panel With LED To Show Operation Condition (shall be finalized by vendor) . | Required
18.2 | Commissioning and two years spare parts shall be provided | Required
18.3 | The Accuracy of all meters shall be better than 1.5% | Required
18.4 | On load break switch-fuse For Battery Banks:Exd type IIC-T3 | Required
18.5 | Training | The Supplier /Vendor shall be assumed the maintenance and repair training course at least for 5 People
18.6 | Battery Room Fan failure (Activated by external Signal ) | Required
19.Electromagnetic Compatibility (EMC)
All DC-UPS units shall comply with the requirements for EMC as defined in IEC 62040-2, in order to ensure:Conducted emissions in both, the power supply input and output of the DC- UPS are controlled within acceptable limits;Any electromagnetic disturbance generated by the UPS and its individual components do not exceed a level which would affect the correct operation of both, radio and telecommunications equipment;
The complete set of battery & battery charger shall be considered for each well. Wellpads are BK-12, BK-15, BK-05, Well 007, Well 046 & BK-14
A serial link communication protocol shall be considered or sending alarms and indications to DCS.
تسهیلات
DATA SHEETS FOR DC CHARGER OF WELL PADS
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0003
D03
بسته کاری
SSGRL
پروژه
BK