| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| DATA SHEETS FOR REMOTE CONTROL PANEL نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D02 | Apr. 2023 | AFC | H.Shakiba | M.Fakharian | A.M.Mohseni |  |
| D01 | Jul. 2022 | IFA | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| D00 | May. 2022 | IFC | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:1 |  | Client Doc. Number: F0Z-709031 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for Client Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X |  |  |  | 51 |  |  |  |  |  |
| 2 | X | X | X |  |  |  | 52 |  |  |  |  |  |
| 3 | X | X |  |  |  |  | 53 |  |  |  |  |  |
| 4 | X | X |  |  |  |  | 54 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 55 |  |  |  |  |  |
| 6 |  |  |  |  |  |  | 56 |  |  |  |  |  |
| 7 |  |  |  |  |  |  | 57 |  |  |  |  |  |
| 8 |  |  |  |  |  |  | 58 |  |  |  |  |  |
| 9 |  |  |  |  |  |  | 59 |  |  |  |  |  |
| 10 |  |  |  |  |  |  | 60 |  |  |  |  |  |
| 11 |  |  |  |  |  |  | 61 |  |  |  |  |  |
| 12 |  |  |  |  |  |  | 62 |  |  |  |  |  |
| 13 |  |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 |  |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 |  |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

| Technical Data Sheets For Remote Control Panel |  |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REQUIREMENT | SUPPLIER DATA |
| 1 | Environmental Conditions (Process Basis Design, BK-GNRAL-PEDCO-000-PR-DB-0001) |  |  |
|  | Location | Binak Oilfield in Bushehr Province |  |
|  | Max. Outdoor Ambient Temperature | 52°C |  |
|  | Min. Outdoor Ambient Temperature | 5°C |  |
|  | Direct Sunlight Temperature | 85°C |  |
|  | Maximum Relative Outdoor Humidity | 100% |  |
|  | Altitude | 12.5 m Above Sea Level |  |
| 2 | GENERAL INFORMATION |  |  |
|  | Tag Numbers | RCP-02 (Indoor Safe) |  |
|  | Quantity | 1 Set |  |
|  | Application Standard | IPS-E-EL-100 IPS-M-EL-161 IPS-M-EL-143(3) |  |
|  | Manufacturer | By Vendor |  |
|  | Related Document | Electrical Overall Single Line Diagram “BK-GCS-PEDCO-120-EL-SL-0001” Existent MV Switchgear Expansion Single Line Diagram “BK-GCS-PEDCO-120-EL-SL-0003” Electrical Typical Schematic Diagrams for MV Panel “BK-GCS-PEDCO-120-EL-DG-0001” Wiring Diagram for Interposing Relay Panel (IRP) “BK-GCS-PEDCO-120-EL-DG-0011” |  |
| 3 | ELECTRICAL DATA |  |  |
|  | System Voltage/ Frequency | 400V AC / 50Hz |  |
|  | Voltage Variation/ Frequency Variation | ±10 / ± 5% |  |
|  | Insulation Voltage | 0.6/1KV |  |
|  | No. of Phases / Wires | 1Ph+N+PE |  |
|  | Control Voltage | 110 VDC |  |
|  | Space Heater Voltage | 230VAC |  |
|  | Internal/ External Voltage Supply | External |  |
|  | Bus-Bars Material | Indoor: Heat Shrink Copper Outdoor: Silver Plated Copper |  |
| 4 | ENCLOSURE DATA |  |  |
|  | Enclosure Type | Wall Mounted , Fixed Type, Front Access |  |
|  | Degree of Protection | Indoor: IP 42 |  |
|  | Cable Entry | Bottom via Gland |  |
|  | Material | Painted Sheet Steel |  |
|  | Finish Color | RAL 7032 |  |
|  | Dimensions (HxWxD) | By Vendor |  |
|  | Sheet Steel Thickness (Body/Frame) | Wall Mounted: 1.5mm/2mm |  |
|  | Painting | For Corrosive & Hot Atmosphere |  |
|  | Thickness | Min. 60μ |  |
|  | Type | Epoxy Powder Elector Static |  |
|  | Weight | By Vendor |  |
| 5 | SELECTOR SWITCH |  |  |
|  | Selector Pole | 1 |  |
|  | Selector Position | Position "OPEN-OFF-CLOSE" |  |
|  | Selector Type | Spring Return to Center |  |
| 6 | LABLE |  |  |
|  | Language | English |  |
|  | Material | Stainless Steel-Screwed/Reverted |  |
|  | Main Label (Front / Back) | Engraved / Black Font-White Background |  |
| 7 | PANEL WIRING |  |  |
|  | Manufacturer | By Vendor |  |
|  | Type | CU/PVC/PVC |  |
|  | Power Wire Color | By Vendor |  |
|  | Signal Wire Color (Voltage Presence Indicator) | By Vendor |  |
| 8 | PANEL TERMINAL |  |  |
|  | Manufacturer | By Vendor |  |
|  | Model NO. | By Vendor |  |
|  | Type | Solderless Clamp Type-Flame Retardant |  |
|  | Rated Voltage | According to IEC |  |
|  | Size | Min. 4sqmm |  |
|  | Color | Neutral (Blue) / PE (Green/ Yellow) |  |
| 9 | ACCESSORIES |  |  |
|  | Door Key | Yes |  |
|  | Gland Plate (Undrilled) | Yes |  |
|  | Gland Plate Type (Normal/Non-Magnetic) | Normal |  |
|  | Terminal Lugs | Yes |  |
|  | Signal Lamp ( 110 VDC) | C.B. Closed : Red C.B. Opened : Green C.B Fault : Yellow |  |

Note 1: All required accessories shall be considered by vendor.