## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-MR-0006_D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1885 |  |  | Transmital Date: 20/FEB/2023
Document Title: PMR For Instrument/Plant Air & Nitrogen Packages |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0201-ME-TR-1885 |  |  | Transmital Date: 20/FEB/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-MR-0006_D02 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | برای خشک کننده هوا عبارت" microprocessor based" حذف گردد تا امکان ارائه پیشنهاد های دیگر و بهتر برای سازندگان فراهم شود. -در خصوص کمپرسورهای هوا و ارتباط آنها با خشک کننده های هوا توضیحات به گونه ای اصلاح شود که موارد ذیل مشخص باشد : . مشخص شود که کمپرسور های هوا دارای UCP مختص خود می باشند. .خشک کننده هوا نیز دارای LCP مختص خود باشند . هر کدام از خشک کننده ها فارق از اینکه کدام کمپرسور هوا در سرویس باشد بتواند کار کند. -موارد فوق در مدارک پیوست مرتبط( نقشه های P&ID و SPEC و ... ) لحاظ شود و اصلاحات لازم انجام گردد. |  | 02/2294/30940 | 1402/01/30 | -اصلاح گردید به as minimum micro processor based -اصلاح گردید و توضیحات لازم اضافه شده است -موارد فوق در مدارک پیوست مرتبط لحاظ و اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: |  |  |  |  | Date: 30/APR/2023