## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-MR-0006_D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1885 |  |  | Transmital Date: Feb-20-2023
Document Title: PMR For Instrument/Plant Air & Nitrogen Packages |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0112-ME-TR-1885 |  |  | Transmital Date: Feb-20-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-MR-0006_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
QC/QA COMMENTS:
1 | در بند 5.1.1: -عبارت "QA Organization" به "QA/QC Organization Chart" تغيير يابد. |  | BK-SUR-ENG-MEC-01-07139 | 2023-03-07 | Noted
2 | در بند 6: -عبارت "QC Plan" و "Quality Control Plan" به "Inspection and Test Plan (ITP)" تغيير يابد. -دستورالعمل انتخاب سطح بازرسي كالا و تجهيزات به شماره مدرك ICE-EID-MI-SP02-REV-01 اضافه گردد. |  | BK-SUR-ENG-MEC-01-07139 | 2023-03-07 | Noted
3 | در خط دوم بند7، عبارت "Supplier" به عبارت "Vendor" تغيير يابد. |  | BK-SUR-ENG-MEC-01-07139 | 2023-03-07 | Noted
4 | در جدول Attachment 2: -در رديف 1، عبارت "See Attachment 2" حذف گردد. - عبارت "List of Documents will be Finalized in VPIS" در نوتها اضافه گردد. - مدارك SAT Procedure اضافه گردد. - در رديف 084، عبارت "5.1.3" حذف گردد. |  | BK-SUR-ENG-MEC-01-07139 | 2023-03-07 | Noted
5 | لزوم ارائه مدارك ITP, QCP, MPS توسط سازنده قبل از برگزاري جلسه PIM در مدرك درج گردد. |  | BK-SUR-ENG-MEC-01-07139 | 2023-03-07 | Noted
INSTRUMENT COMMENTS:
| عبارات “A PLC based UCP mounted in control room for air compressor as authorized master logic controller of complete air package. Standalone microprocessor based control panel located on dryer skid for all required signaling, local logic, monitoring and etc. which shall be connected to control room mounted UCP of air compressor. UCP shall be connected to the PCS, ESD, for required monitoring, control functions and shutdowns as per P&ID. UCP panel door shall including alarm, trip and interlock logic; annunciator lamp and buzzer; push button switches; Terminal box, if UCP is control room mounted , required LCP for local command isrequired.” در خصوص پكيج هوا و عبارت "A PLC based UCP mounted in control room for each Nitrogen package. UCP shall be connected to the PCS, ESD, for required monitoring, control functions and shutdowns as per P&ID. UCP panel door shall including alarm, trip and interlock logic; annunciator lamp and buzzer; push button switches; Terminal box, if UCP is control room mounted , required LCP for local command is required." در خصوص پكيج N2 با مدرك Block Diagram for GCS Control تناقض دارد و مورد تاييد اين امور و كارفرما نيز نمي باشد. براي پيشبرد گام بعدي مهندسي پيشنهاد مي گردد كه اين موارد از مدرك حذف و به مدارك مربوط به spec و Block Diagram ارجاع داده شود. |  | BK-SUR-ENG-MEC-01-07139 | 2023-03-07 | مورد ذکر شده مطابق آخرین توافقات در Spec های ضمیمه شده به این مدرک و سایر مدارک مهندسی از جمله P&ID و یاگرامهای کنترلی …پیاده شده است. به دلیل تاکید بیشتر و جلوگیری از خطا متن صریح آن در PMR نیز آورده شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature | H.Naserizadeh |  |  | Clarified By: H.Adineh | Signature
Date: 30/APR/2023