## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0002-D05 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1807 |  |  | Transmital Date: 18-Jan-2023
Document Title: Electrical Typical Schematic Diagrams For LV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-EL-TR-1807 |  |  | Transmital Date: 18-Jan-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DG-0002-D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | کنتاکت خودنگهدار در مسیر تست به جهت انجام تست های حفاظتی الزامی است، با افزودن کنتاکت خودنگهدار نیازی به اضافه کردن پوش استاپ نمی باشد. از پوش استاپ ابتدای مسیر قطع مدار میتوان استفاده نمود. |  | 1401-2294-431967 | 1401-11-11 | کنتاکت خودنگهدار در مسیر تست قرار داده شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Jan-23 |  |  |  |  | Date: