## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-PR-PI-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1758 |  |  | Transmital Date: 1/2/2023
Document Title: P&ID for Potable Water Tank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1758 |  |  | Transmital Date: 1/2/2023
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-PR-PI-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق شرح کار پروژه مخزن می بایست بر روی استراکچر فلزی قرار گیرد |  | 1402-2294-34538 | 1402/02/04 | اعمال می گردد.
2 | مطابق با شرح کار پروژه مخزن می بایست در ارتفاع 15 متری قرار گیرد |  | 1402-2294-34538 | 1402/02/04 | اعمال گردید.
3 | جنس متریال مورد استفاده مورد قبول این امور نمی باشد لذا جنس مخزن می بایست فلزی در نظر گرفته شود. |  | 1402-2294-34538 | 1402/02/04 | مورد تایید است.
4 | جهت مخزن مذکور می بایست عایق در نظر گرفته شود ضمنا در قسمت NOTE به این مهم اشاره شود. |  | 1402-2294-34538 | 1402/02/04 | در قسمت توضیخات تانک ارائه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021