## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0005_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1625 |  |  | Transmital Date: 28-Nov-2022
Document Title: Electrical I/O Signal List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0109-EL-TR-1625 |  |  | Transmital Date: 28-Nov-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-LI-0005_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -I/O List for control system -I/O List for ESD system -P&ID document base on HAZOP study. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
2 | The signals between DCS (IRP) and MV/LV switchgears incomings, Coupling and outgoing feeders, AC/DC UPS, generator Control panel, Transformers alarm window, packages control panel, etc shall be added to list. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
3 | The signals between RCP and MV switchgear incomings, Coupling and outgoings shall be added to list. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
4 | Type of Output/Input signals (DO/DI/AO/AI), type of connection (Hardwire/Serial Link) and type of signals (Dry/Wet) shall be added and specified. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | با توجه به اینکه ماهیت تابلوی IRP استفاده از منابع تغذیه جدا برای کنتاکتها می باشد لذا تمامی کنتاکتها خشک بوده و کنتاکت WET استفاده نمی شود. |  |  | Noted and Closed.
5 | The electrical I/O list is for signals between MV/LV switchgears (Incoming, Coupling and outgoing feeders), etc. and IRP panel, so columns "from" and "to" shall be modified. |  | BK-SUR-ENG-ELE-01-04993 | 2022-07-05 | اعمال گردید. |  |  | Noted and Closed.
6 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11
6-1 | Signal between F&G and DC&AC UPS as title "Inhibit to Boost" and "Battery Fan" shall be modified. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید.
6-2 | Stop/Start command shall be added for 11/3.3 KV SWGR-Transformer Feeder-Q4 between RCP and MV switchgear. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید.
6-3 | Connection points between RCP and MV spare feeders shall be added. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید.
7 | signals related to UPS and Chargers shall be finalized based on manufacturer data. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | همانطور که در مدرک SLD مربوط به UPS نشان داده شده است، سازنده موظف است سیگنالهای مرود نیاز را لحاظ نماید.
8 | As per diesel oil system P&ID, remote stop command from DCS is not required for diesel oil pump, P-2206. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | اعمال گردید.
9 | As per Glycol Sump Drum P&ID, ESD trip is required for glycol sump pump, P-2104. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | کامنت وارد هست. باید در نقشه Typical فیدر موتور مربوطه، این موضوع در نظر گرفته شود. در مدرک ESD I/O List وجود دارد.
10 | regarding close drain P&ID, it seems remote start is required for P-2202A/B and P-2203A/B. it shall be rechecked by Process and modified if required. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | سیگنال Start برای پمپ های P-2202 و P-2203 باید اضافه شود. بدیهی است در طراحی تابلوی برق (فیدر موتور)، توسط پیمانکار مربوطه، Start Command باید وجود داشته باشد.
11 | regarding LP flare system, P&ID, it seems remote start is required for P-2201A/B. it shall be rechecked by Process and modified if required. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | مطابق پاسخ آیتم شماره 10: سیگنال Start برای پمپ های P-2201 باید اضافه شود. بدیهی است در طراحی تابلوی برق (فیدر موتور)، توسط پیمانکار مربوطه، Start Command باید وجود داشته باشد.
12 | Regarding Gas Compression Dehydration Package P&ID, lean glycol pumps signals shall be added to signal list. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | در I/O List ، سیگنالها مطابق P&ID دیده شده اند: سیگنال پمپهای 2103 با Tag Number های 2161 وجود دارند.
13 | Signal between MCC and packages LCP shall be added to this document as per manufacturer documents. (for example some signals have been shown in the corrosion inhibitor package P&ID. ) |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | سیگنالهای بین MCC و پکیج بعد از نهایی شدن وندور و تعیین لیست سیگنال توسط سازنده در نظر گرفته خواهد شد.
| Instrument Comment: پيرو جلسه مورخ 08/09/1401 با حضور ذينفع اصلي و پيمانكار (صورتجلسه به پيوست آمده است) مقرر گرديد سيگنالهاي مرتبط با ESD كمپرسور از طريق IRP نيز ديده شود،لذا موارد بايستي در مدارك مرتبط بررسي و شفاف سازي شود. |  | BK-SUR-ENG-ELE-01-06387 | 2022-12-11 | سیگنالهای کمپرسور بعد از تعیین توسط سازنده مشخص خواهد شد و در تابلوی LV مربوط به بارهای Auxilary لحاظ خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 11-Dec-22 |  |  |  |  | Date: