## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LI-0006_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1726 |  |  | Transmital Date: 25 Dec 2022
Document Title: Set Point & Alarm List - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1726 |  |  | Transmital Date: 25 Dec 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-LI-0006_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مدرک PFD نیز به مدارک مرجع اضافه گردد. |  | 01/2294/415315 | 1401/11/1 | با توجه به نظر کار فرمای محترم اعمال گردید.
2 | مبنای در نظر گرفته شده جهت میزان دبی کمترین و بیشترین بیان گردد. |  | 01/2294/415315 | 1401/11/1 | مقادر دبی برای حالت HHLLو HHL به ترتیب برابر با 110% و 105% بیشینه میزان جریان، و برای حالت LLLL و LLL به ترتیب برابر با 30% و 35% کمینه ی میزان در نظر گرفته شده است.
3 | نقاط تنظیمی فشار شیرهای ایمنی ورودی چندراهه بصورت ذیل در نظر گرفته شود: نقطه تنظیمی فشار بالای شیر ایمنی ورودی نفت چاهها = 1050 پام نقطه تنظیمی فشار پایین شیر ایمنی ورودی نفت چاهها = 100 پام |  | 01/2294/415315 | 1401/11/1 | با توجه به نظر کار فرمای محترم اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: