## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LI-0006_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1726 |  |  | Transmital Date: 25 Dec 2022
Document Title: Set Point & Alarm List - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1726 |  |  | Transmital Date: 25 Dec 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-LI-0006_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | اعداد Setpoint فشار برای HH و LL با توجه به نزدیک بودن به فشار عملیاتی و تبعات بستن شیر EDS وردی بر روی Shutdown چاهها، نیاز به بازنگری دارد. |  | BK-SUR-ENG-INS-01-06630 | 2023-01-08 | اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 8 Jan 2023 |  |  |  |  | Date: