## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0004-D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1237 |  |  | Transmital Date: 30-Aug-2022
Document Title: Calculation Note For UPS System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1237 |  |  | Transmital Date: 30-Aug-2022
[5 empty] | CRS No: PEDCO-CRS- BK-GCS-PEDCO-120-EL-CN-0004-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | AC Load Consumption of instrument & control systems shall be specified in table by details. Meanwhile reference document (Instrument consumption list) for above mentioned table has not been submitted yet and it shall be clarify the rated load power has been considered base on which document. (It is necessary to refer to basic electrical equipment list and show that 10KW has been considered for AC UPS, not 32KW) |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | با توجه به اینکه بار های UPS توسط بخش ابزاردقیق در حال نهایی سازی می باشد. هر گونه تغییر، در ویرایش های بعدی مدرک لحاظ خواهد گردید. |  |  | See below item 9
2 | The calculation shall be updated base on last revision of BaSiCs software (V3.1.2) and above mentioned comment. It shall be checked to optimized battery sizing and battery rack dimention and prevent go oversizing. |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | اعمال گردید. |  |  | Noted&Closed.
3 | A separate section with title "number of battery cells" shall be added and number of battery cells shall be calculated base on minimum battery voltage limit (99V) and battery end voltage (1.14V). |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | در قسمت 6.3 محاسبه تعداد باتری مشخص شده است. |  |  | Noted&Closed.
4 | Following items shall be added and specified in section 5: • Spare capacity • Voltage of batteries • The float charge voltage • The boost charge voltage • Inverter Efficiency • Battery Bank Nominal Voltage (DC link voltage) • Battery Type • The number and capacity of charger, battery and inverter • Input and output voltage, frequency and variation |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | ظرفیت اضافه در محاسبات در نظر گرفته شده است باقی موارد لحاظ گردید.لازم به ذکر است ولتاژ شارژ سریع توسط سازنده تعیین خواهد شد. |  |  | Noted&Closed.
5 | Page 7, Section 6.2: According to "Specification for AC UPS system BK-GNRAL-PEDCO-000-EL-SP-0003" document, 2x100% battery banks, vented Ni-cd type shall be considered. |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | اعمال گردید. |  |  | See below item 10
6 | Pages 7&8, Section 6.3: Letter "N" and related description shall be deleted from formula. It is not applicable for AC UPS configuration of this project. |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | براساس نقطه نظرات کارفرمای محترم فرمول محاسبات به روز رسانی گردید. |  |  | Noted&Closed.
7 | BasiCs reports shall be added to section 8 with following title: Attachment #1_SAFT Catalogue and Data Sheet (for SBM Type Batteries) Attachment #2_SAFT BaSiCs Results for 110VAC UPS Battery Calculation Attachment #3_ SAFT BaSiCs Results for Stand Proposal |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | اعمال گردید. |  |  | Noted&Closed.
8 | BaSiCs Ventilation report shall be attached in order to sizing battery room ventilation fan. |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | در مدرک متناظر با HVAC محاسبات در نظر گرفته خواهد شد |  |  | Noted&Closed.
9 | Ref. above item 1: According to our previous telephone conversation and comment, the rated power in basic documents shall be used to UPS sizing before prerequisite documents are submitted. Consideration shall be given that this document effect on some important documents such as architectural drawing of control building especially in battery room dimention. So this document shall be revised base on rated power in basic document. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | مطابق با ترنمیتال 633 (لیست بارز ابزاردقیق در ایستگاه تقویت فشار) میزان بار UPS حدود 30 کیلو وات است که این عدد ملاک محاسبه خواهد بود. از این رو در صورت تغییر در بارها ابزاردقیق این مدرک مورد بازنگری قرار می گیرد. |  |  | Will be checked later.
10 | Ref. above item 5: Following sentences shall be modified: "Regarding to the specification for UPS System, the size of battery has calculated at 50% capacity for each battery bank." |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | اعمال گردید. |  |  | Noted&Closed.
11 | با توجه به نامه شماره 47232 مورخ 1401/02/11 (پاسخ ذينفع اصلي پروژه به ترنسميتال 852) مبني بر عدم تاييد مدرك I&C Power consumption و همچنين نقطه نظر واحد ابزاردقيق پترو ايران به شرح زير، امكان بررسي محاسبات در اين مقطع وجود نداشته و لذا مقتضي است پيرو مذاكرات قبلي تا زمان نهايي شدن مدرك مذكور از ارسال مجدد اين مدرك خودداري شود. -با توجه به نهايي نشدن مدرك I&C Power consumption و نقطه نظرات موجود در فايل ضميمه T-0861 ميزان بار مورد نياز تجهيزات ابزاردقيق نهايي نمي باشد. |  | BK-SUR-ENG-ELE-01-04178 | 2022-05-09 | این مدرک بر اساس آخرین لیست بار بخش ابزاردقیق محاسبه شده است. در صورت وجود هرگونه تغییر در مصارف آینده، این مدرک به روزسانی خواهد شد. |  |  | See below item 12.
12 | See above item 11: با توجه به نامه شماره 91107 مورخ 1401/03/17 (پاسخ ذينفع اصلي پروژه به ترنسميتال 861) مبني بر عدم تاييد مدرك I&C Power consumption و همچنين نقطه نظر واحد ابزاردقيق پترو ايران به شرح زير، امكان بررسي محاسبات در اين مقطع وجود نداشته و لذا مقتضي است پيرو مذاكرات قبلي تا زمان نهايي شدن مدرك مذكور از ارسال مجدد اين مدرك خودداري شود. _بازگشت به TR-1237 و مذاكرات صورت گرفته با ذينفع اصلي در اهواز، لازم است مدرك و مستندات مرتبط با I&C power consumption جهت بررسي و تاييد ذينفع اصلي بروزرساني و مجدد ارسال گردد. لازم به ذكر است پيرو جلسات و پاسخ هاي قبلي مقدار عدد ذكر شده براي UPS مورد تاييد اين بخش نمي باشد و تنها در صورت موافقت و تاييد ذينفع اصلي قابل بررسي و لحاظ كردن مي باشد. |  | BK-SUR-ENG-ELE-01-05478 | 2022-08-16 | همانطور که مستحضر هستید مدرک محاسباتی UPS در کامنت شیت شماره 205602 بر روی ترنسمیتال 1237، AN شده است. همچنین این مدرک از لحاظ نحوه محاسبات مورد تایید کارشناسان محترم شرکت پترو ایران می باشد لذا از آنجا که براساس ترنسمیتال 1692 آخرین محاسبات بخش ابزاردقیق با اعداد این مدرک همخوانی دارد این مدرک به صورت نهایی ارسال می گردد. در صورت هر گونه تغییر در مدرک ابزاردقیق این مدرک ویرایش خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 17-Aug-22 |  |  |  |  | Date: