## TBE for TG
نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني مربوط به موقعیت W008N
Contract No: 9184 – 073 - 053 |  |  | TBE For Temperature Gauge
|  |  | Project Code |  | Package | Company code |  | Scope | Disc Code | Doc. Code | Sequence No. |  | Rev. Code
|  |  | BK |  | W008N | PEDCO |  | 110 | IN | TB | 0002 |  | D02
REQ. NAME : |  | MR for Temperature Gauge |  | BIDDER:
REQ. NO. : |  | RR-00-PS-110-IN-MR-0030 |  | NAME: |  |  | سنگان صنعت |  |  | تجهیزات فراصنعت آرمان |  |  | ساعی سامانگر صنعت سبز (4S)
REQ. REV. : |  | D04 |  | QUOTATION NO.: |  |  | 1400-P-8717-Rev01 |  |  | 264 ب |  |  | 140107011
EQUIPMENT TYPE : |  | Temperature Gauge |  | QUOTATION DATE: |  |  | 2022-10-19 |  |  | 1401-12-01 |  |  | 1401/07/27
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED
[7 empty] | A |  |  | B |  |  | D
A | Scope of Work And Supply
1 | Tag Number |  |  | TG/TW-1601
2 | Scope of Work And Supply |  |  | Temperature Gauge |  |  | Yes |  |  | Yes |  |  | Yes
3 | Delivary Date |  |  | B.V. |  |  | 90 working Days after advanced payment and approved technical documents |  |  | Not specified |  |  | Not specified
4 | Delivary Place |  |  | Ex.Work |  |  | EX.WORKS |  |  | Not specified |  |  | Not specified
5 | Bid Validity Period |  |  | B.V. |  |  | 30 days |  |  | Not specified |  |  | Not specified
6 | GUARANTEE |  |  | Requisition eighteen (18) months from the date of the Installation and Commissioning or twenty-four (24) months after the date of delivery of materials (whichever comes earlier) |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor
7 | MANUFACTURER (VENDOR LIST) |  |  | AVL |  |  | Submitted |  |  | Yes |  |  | Confirmed by Vendor
8 | SPARE PARTS |  |  | 5% complete set (3 Set PG & 1 Set TG for all wells) |  |  | Submitted |  |  | Submitted |  |  | Confirmed by Vendor
B | Technical Requirements
1 | Environmental / Process Condition |  |  | According to data sheet |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor
2 | Thermometer Type |  |  | Bimetal / Filled type (As requested) |  |  | Yes |  |  | Yes |  |  | Yes | Confirmed
3 | Calibrated Range |  |  | As requested |  |  | Yes |  |  | Yes |  |  | Confirmed in TCL | Confirmed
4 | Dial Size |  |  | 150 mm |  |  | 150 mm |  |  | 150 mm |  |  | 150 mm | Confirmed
5 | Dial Color |  |  | White with black Letter |  |  | Yes |  |  | Yes |  |  | Confirmed by Vendor | Confirmed
6 | Case Material |  |  | Stainless Steel 304 |  |  | St. St. 304 |  |  | Stainless Steel 304 |  |  | Stainless Steel 304 | Confirmed
7 | Process Connection Size/ rating |  |  | 1 1/2 RTJ,/ API 3000 |  |  | 1 1/2" #1500 RTJ |  |  | 1 1/2 RTJ,/ API 3000 |  |  | 1 1/2 RTJ #900 | Confirmed
8 | Eng. Unit |  |  | °C/ °F |  |  | Not Specified |  |  | Yes |  |  | Yes | Confirmed
9 | Accuracy |  |  | Better than ± 1% of full span |  |  | 1% of F.S. |  |  | Yes |  |  | Yes | Confirmed
10 | Pointer Color / Material |  |  | Black / Metallic |  |  | Confirmed by Vendor |  |  | Aluminum Pointer |  |  | Confirmed by Vendor | Confirmed
11 | Stem Type / Material |  |  | Threaded / 316 SS |  |  | Yes |  |  | Yes |  |  | Threaded / 316 SS | Confirmed
12 | Stem Diameter |  |  | 6 mm |  |  | 6 mm |  |  | 6 mm |  | Confirmed | 6 mm | Confirmed
13 | Ingress Protection |  |  | IP65 |  |  | IP 65 |  |  | IP 65 |  | Confirmed | IP 65 | Confirmed
14 | Window Material |  |  | Shatterproof Glass |  |  | Shatterproof & safety glass |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor | Confirmed
15 | Zero Adjustment |  |  | Pointer |  |  | Confirmed by Vendor |  |  | Yes |  |  | Confirmed by Vendor | Confirmed
16 | Over range Protection |  |  | 1.5 times the maximum scale. |  |  | Confirmed by Vendor |  |  | Yes |  |  | Confirmed by Vendor | Confirmed
17 | Connection |  |  | Every Angle |  |  | EVERY ANGLE (Adjustable) |  |  | Yes |  |  | Yes | Confirmed (Back )
18 | External Calibration Adjustment |  |  | Required |  |  | Confirmed by Vendor |  |  | Yes |  |  | Confirmed by Vendor | Confirmed
19 | Head Type |  |  | Oriantable Head |  |  | Yes |  |  | Yes |  |  | Yes | Confirmed
20 | Thermowell |  |  | Tapered Drilled Bar Stock |  |  | Yes |  |  | Tapered Drilled Bar Stock |  |  | Tapered Drilled Bar Stock | Confirmed
21 | Well conn. & Flange Material |  |  | As requested & Stainless Steel 316 |  |  | Yes |  |  | Yes |  |  | Yes | Confirmed
22 | Thermowell Connection to thermometer |  |  | 1/2" NPTF |  |  | 1/2" NPT-Female |  |  | 1/2" NPTF |  |  | 1/2" NPTF | Confirmed
23 | In Complaince with Nace Standard |  |  | As requested |  |  | Yes |  |  | Yes |  |  | Yes | Confirmed
24 | Insertion Length (U) mm |  |  | As requested |  |  | Yes |  |  | Yes |  |  | No | Confirmed
25 | SS Name Plate |  |  | As requested |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor | Confirmed
26 | Accessories for installation for remote type |  |  | As requested |  |  | N/A |  |  | N/A |  |  | N/A | Confirmed
C | Test and Inspection
1 | Test and Inspection |  |  | Project IDS, Requisition |  |  | Submitted |  |  | Confirmed to Submit |  |  | Confirmed to Submit
D | Document Requirements
1 | Country Of Origin |  |  | Contract |  |  | Made in iran |  |  | IRAN |  |  | IRAN
2 | Wake Frequency Calculaton |  |  | Requisition |  |  | Yes |  |  | Confirmed to Submit |  | NO Needed Velocity is 0 | Confirmed to Submit | NO Needed Velocity is 0
3 | Material Test / Calibration Certificate |  |  | Requisition |  |  | Confirmed by Vendor |  |  | Confirmed to Submit |  | NO Needed Velocity is 0 | Confirmed by Vendor | Confirmed
4 | Level of Similar Experience in past 10 years |  |  | Vendor 's Quotation |  |  | Refrence list submitted |  |  | Not Submitted |  |  | Not Submitted
F | Deviations / Alternatives
1 | Deviations (if any) |  |  | signed and stamped |  |  | Attached. |  |  | Not Submitted |  |  | Not Submitted
2 | Manufacturer's Location |  |  | - |  |  | Tehran - Qom highway |  |  | Esfahan-IRAN |  |  | Shiraz-IRAN
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  |  | shall be submitted |  |  | Submitted |  |  | Confirmed to Submit |  |  | Confirmed to Submit
2 | Standard certificates |  |  | shall be submitted |  |  | Submitted |  |  | Confirmed to Submit |  |  | Confirmed to Submit
3 | Filled TBE |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  |  | Submitted | Submitted
4 | Summary sheets |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  |  | Not Submitted
5 | Subvendor list (if any) |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  |  | Confirmed to Submit
6 | Reference list |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  |  | Not Submitted
7 | Catalouges |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  |  | Confirmed to Submit
8 | Datasheet/ Drawing |  |  | shall be submitted |  |  | Submitted |  |  | After PO |  |  | After PO
9 | Order code (Part No.) |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  |  | Not Submitted
GENERAL ACCEPTANCE FOR QUOTATION: | [6 empty] | ACCEPTED |  |  | ACCEPTED |  |  | NOT ACCEPTD
Notes:
A : ACCEPTABLE (TECHNICALLY MEETS REQUIREMENT)
NA: NOT ACCEPTABLE (TECHNICALLY DOES NOT MEET REQUIREMENT)
CA: CONDITIONALLY ACCEPTED
INA: INFORMATION NOT AVAILABLE
N/A: NOT APPLICABLE
D02