## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0006-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1248 |  |  | Transmital Date: 03-Aug-2022
Document Title: DC Charger Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1248 |  |  | Transmital Date: 03-Aug-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0006-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به عدم تایید لیست بار سیستم 24VDC توسط بخش ابزار دقیق ( نامه شماره 47232 مورخ 1401/02/11)، مقتضی است ظرفیت باتری های سیستم (1300AH) پس از تایید مقدار واقعی بار و نهایی شدن مدرک محاسبات اصلاح گردد. |  | 1401-2294-198988 | 1401-06-06 | مدرک سایزینگ از لحاظ نحوه محاسبات مورد تایید کارشناسان محترم کارفرما می باشد لذا از آنجا که براساس ترنسمیتال 1692 آخرین محاسبات بخش ابزاردقیق با اعداد این مدرک همخوانی دارد این مدرک به صورت نهایی ارسال می گردد. در صورت هر گونه تغییر در مدرک ابزار دقیق این مدرک ویرایش خواهد شد. شایان ذکر است کامنت کافرمای محترم مرتفع گردید.
2 | سطح مقطع کابل اتصال بدنه دستگاه های شارژر مطابق نقشه نمونه تک خطی ارسالی با نامه شماره 352430 مورخ 1400/10/16 به 70mm2 افزایش یابد. |  | 1401-2294-198988 | 1401-06-06 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 17-Aug-22 |  |  |  |  | Date: