## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0004_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0950 |  |  | Transmital Date: 15-May-2022
Document Title: Lighting & Small Power Layout For Building & Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0950 |  |  | Transmital Date: 15-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-PY-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on following documents: -Calculation note for indoor area lighting system -Architectural Drawing For Buildings and shelters -HVAC system layout for buildings -Hazardous area classification layout |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | اعمال گردید.
2 | Following documents shall be added as reference documents: -Calculation note for indoor area lighting system -Architectural Drawing For Buildings and shelters -HVAC system layout for buildings -Hazardous area classification layout |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | اعمال گردید.
3 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28
3-1 | Lighting panel installation location shall be shown and type of lighting panel (Ex or Non-Ex) shall be specified based on hazardous area classification layout. Meanwhile type of installation (Wall mounted Surface/Flush mounted for indoor lighting panel or structural mounted for outdoor lighting panel) shall be specified. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | نوت 4 مربوط به روشنایی شلتر ها مشخص گردید بدین سان چراغ ها بالای جرثقیل سقفی نصب خواهد شد.در مورد ساختمان ها نیز این موضوع عنوان شده است.
3-2 | All equipment in pantry,WC and bathroom shall be considered IP55 and Lighting fixture, outdoor installation in safe area shall be considered IP65,in battery room and outdoor installation in hazardous area shall be considered IP65, for other indoor installation shall be considered IP42. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | اعمال گردید.
3-3 | It shall be clarify cable between split unit and condenser/split unit and socket will be supplied by vendor or not. (Added as note) |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | ساختمان کنترل دارای سیستم هواساز مجزا می باشد که برق مورد نیاز آن در مدرک لیست بار در نظر گرفته شده است. برای ساختمان سوییچگیر نیز فیدر از تابلوی روشنایی به صورت مستقیم تا اسپلیت در نظر گرفته خواهد شد. این موضوع در دیاگرام تک خطی نشان داده خواهد شد.
3-4 | Related switch for outgoing around of control bulding lifgting fixturers shall be shown in layout. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | این چراغها با فتوسل روشن خواهند شد
3-5 | It shall be clarify why battery back up lighitng fixturers has not been considered in battery room. Meanwhile for battery back up lighting fixturers 4 core cable or seperat wire shall be considered for battery from before switch. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | مطابق با صحبتهای انجام شده با آقای سعادتیان مقرر گشت برق مورد نظر این ساختمان از فیدر اضطراری تأمین گردد. در نتیجه نیاز به چراغهای با باتری نمی باشد.
4 | Typical installation detail for each lighting equipment shall be added and specified base on "Typical Installation Details & Notes For Lighting System". |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | به مدرک تیپیکال روشنایی اشاره شده است.
5 | It shall be clarify, EDB-050 for CO2 for switchgear building is new or existing lighting panel. If it is existing lighting panel below items shall be checked and modified if required: 1-NISOC confirmation 2-Existing feeders shall be shown and the rated current shall be checked that is sufficient or not. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | تابلوی شماره 50، تابلوی موجود در سوییچگیر می باشد. در صورت عدم امکان استفاده از این تابلو، می بایست یک فیدر از تابلوهای جدید به تابلوی روشنایی در این ساختمان اضافه نمود.
6 | According to basic electrical design criteria, discharge capacity for battery back up lighting fixturers shall be at least half an hour. So it shall be recheked and modified. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | مطابق با صحبتهای انجام شده با آقای سعادتیان مقرر گشت برق مورد نظر این ساختمان از فیدر اضطراری تأمین گردد. در نتیجه نیاز به چراغهای با باتری نمی باشد.
7 | It shall be checked that welding sockets in layout needs to JB or not base on related incoming cable and cable between them. Meanwhile IP for WS shall be specified, too. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | JB مورد نیاز در نمودار درختی و MTO آن در نظر گرفته شده است.
8 | There is conflict between block diagram and layout from point used JB view. If JB will be used in lighting system, so type of JB shall be modified base on location of installation. For example in compressor shelter JB shall be Exd IIB T3, IP65 and in utility shelter shall be WP,IP55. (The legend shall be modified.) |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | JB مورد نیاز در نمودار درختی و MTO آن در نظر گرفته شده است.
9 | No. of emergency lighting fixturers in control room shall be modified base on electrical design criteria (50% of fixturers). Meanwhile the battery back up lighting fixturers arrangement in control room can be modified in a way that can be installed on top of work station. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | مطابق با صحبتهای انجام شده با آقای سعادتیان مقرر گشت برق مورد نظر این ساختمان از فیدر اضطراری تأمین گردد. در نتیجه نیاز به چراغهای با باتری نمی باشد.
10 | Mounting height of High bay lighting fixturers, soecket and push button in shelter lighting layout, lighting fixturers in battery room, outdoor control building lighting fixturers, etc shall be specified. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | نوت مربوط به ارتفاع نصب تجهیزات در مدرک اضافه شده است.
11 | According to lighting layout, all socket in pantry room will be supllied by emergency feeder. It is recommended that emergency socket be considered only in rooms that are really required or modified NO. of emergency socket. Meanwhile in control room has not been considered emergency socket. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | مطابق با صحبتهای انجام شده با آقای سعادتیان مقرر گشت برق مورد نظر این ساختمان از فیدر اضطراری تأمین گردد. در نتیجه نیاز به چراغهای با باتری نمی باشد.
12 | There is conflict between this document and I&C power consumption summary from point of No. of UPS socket view. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | اصلاح گردید.
13 | Number of lighting fixturers for transformer shelter/Co2 room and Capacitor room has been shown on layout base on which calculation. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | محاسبات تکمیل شده است و بر اساس آن جانمایی روشنایی مشخص گردیده است.
14 | IP for socket and switch shall be specified base on installation location. For example in transformer shelter/WC/Pantry and bathroom shall be IP55. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | مطابق با کامنت کارفرمای محترم IP ها به روزرسانی شده
15 | Type of protection of lighting fixturers/switch and fan in battery room shall be Exd IIC T3, IP65. Meanwhile one socket shall be added in battery room as above mentioned electrical characteristics. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | اصلاح گردید.
16 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-ELE-01-04448 | 2022-05-28 | در صورت وجود کامنت، موارد در نظر گرفته خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 28-May-22 |  |  |  |  | Date: