## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0006-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1248 |  |  | Transmital Date: 03-Aug-2022
Document Title: DC Charger Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1248 |  |  | Transmital Date: 03-Aug-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0006-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on DC charger calculation and cable sizing documents. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | مدرک محاسباتی باتری شارژر مورد بازبینی قرارگرفت و مطابق با آن، تغییرات در این مدرک لحاظ گردید. |  |  | See below item 10
2 | Single line diagram for 24VDC and 110VDC shall be considered separately in this document because according to basic design criteria (Appendix 1&3), both of them has the same configuration but the outgoing feeders, charger size, etc are different from each other. Meanhile note 2 shall be deleted. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | اعمال گردید و نقطه نظر شماره 2 حذف گردید. |  |  | Noted&Closed.
3 | According to scope of work, all existing and new MV and LV switchgear DC loads shall be fed by new 110VDC UPS, so the 110DC UPS outgoing feeders shall be modified. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | مطابق با مذاکرات انجام شده، فیدرهای خروجی تابلوی توزیع DC مورد بازبینی قرار گرفت. |  |  | Noted&Closed.
4 | Some technical characteristics of equipment shall be added and specified on single line diagram such as rated charger size, rated voltage/short circuit level/rated current/Incoming CB size of DC distribution board, "Exd IIC T3" for fuse box, capacity/back up time/number and type of battery, size of CB and Transformers, the cable size and type between fuse box and battery/fuse box and UPS/Incoming and outgoing feeders, voltmeter and ammeter range and outgoing feeder power. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | مطابق با مذاکرات انجام شده، برخی از پارامترهای اصلی مشخص گردید. سایزینگ برخی ادوات نیز به سازنده واگذار شد. |  |  | See below item 11
5 | Following items shall be added as notes: - Interlocks will be provided to inhibit battery boost charge if battery room ventilation is out of service. -Automatic battery isolation facility shall be provided for incoming MCCB of battery bank. incoming MCCB of battery bank shall be open when F&G system send battery insulation signal to the UPS. -An earth fault monitoring shall be considered for every 10 feeders for easy of finding faulty branch. -Metering and protection system shall be completed based on ac ups specification and detailed information shall be indicated On vendor drawing. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | اعمال گردید. |  |  | Noted&Closed.
6 | As per baisc design criteria appendix 1 and 3 surge arrester shall be considered for incomings. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | اعمال گردید. |  |  | Noted&Closed.
7 | According to basic electrical design criteria (Appendix 1&3) PT ( 400/110) with suitable fuse shall be considered for incoming voltmeters. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | بر اساس کامنت کارفرمای محترم، پیکربندی سیستم DC تغییر پیدا کرد و موارد بر روی مدرک اعمال گردید. |  |  | Noted&Closed.
8 | The body of DC charger panel shall be earthed directly from two point. It shall be shown. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | بر اساس کامنت کارفرمای محترم، پیکربندی سیستم DC تغییر پیدا کرد و موارد بر روی مدرک اعمل گردید. |  |  | Noted&Closed.
9 | The symbol of MCCB and MCB for incoming and outgoing feeders of DC distribution board shall be different from each other in single line diagram. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | بر اساس کامنت کارفرمای محترم، پیکربندی سیستم DC تغییر پیدا کرد و موارد بر روی مدرک اعمل گردید. |  |  | Noted&Closed.
10 | Ref. item 1 above: This document shall be revised base on comment on DC UPS calculation. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | پیرو مذاکرات انجام شده در جلسات با کارشناسان کارفرما و شرکت پترو ایران، ترنسمیتال 852 ملاک طراحی بخش برق قرار گرفته است و در نتیجه آن، ویرایش جدید مدارک DC CHarger (محاسبات، تک خطی و داده برگ) تولید خواهد شد |  |  | See below item 15.
11 | Ref. item 4 above: Rated busbar current of distribution panel shall be specified. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید. |  |  | See below item 16-1.
12 | Feeder for emergency bus (New/Existing) shall be considered seperatly. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید. |  |  | Noted&Closed.
13 | Some rows such cable size, type and tag shall be added for tables below distribution panels and shall be filled base on cable list. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید. |  |  | Noted&Closed.
14 | This document shall be revised and reissued just in case of prerequisite documents such as F&G power consumption list and profile issued based on Vendor recommendation. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | بعد از نهایی شدن قرارداد با وندور، لیست بار سیستم f&g مورد بازنگری قرار خواهد گرفت و در صورت وجود هر گونه تغییر، مدرک ویرایش میگردد. |  |  | See below item 15.
15 | See above item 10 and 14: This document shall be revised base on comments on DC charger claculation document as below: |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17 | این مدرک از لحاظ نحوه محاسبات مورد تایید کارشناسان محترم کارفرما می باشد لذا از آنجا که براساس ترنسمیتال 1692 آخرین محاسبات بخش ابزاردقیق با اعداد این مدرک همخوانی دارد این مدرک به صورت نهایی ارسال می گردد. در صورت هر گونه تغییر در مدرک ابزار دقیق این مدرک ویرایش خواهد شد. شایان ذکر است کامنت کافرمای محترم مرتفع گردید.
15-1 | كامنت ابزاردقيق: بازگشت به نامه شماره 5073 با موضوع "شارژ باطري هاي فايرآلارم و باتري هاي مربوطه" مورخ 08/03/1401، در خصوص محاسبات وضعيت DC Charger سيستم F&G بايستي شفاف سازي گردد. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17
15-2 | Transmittal 852 has been rejected by NISOC and commented (C3) by PEDCO Instrument. Therefor DC charger / AC UPS calculation and other related documents shall not be issued before prerequisite document (I&C power consumption) approval by PEDCO Instrument department. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17
16 | According to our telephone conversation following items shall be modified: |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17
16-1 | See above item 11: The rated current of bus bar and incoming CB for DC distribution panel (110VDC/24VDC) shall be rechecked and modified base on 110VDC power consumption and instrument power consumption list. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17 | توان 110 ولت مورد نیاز تابلو های MV , LV پیشتر به تایید آن کارفرمای محترم رسیده است و براساس آن محاسبه باتری های سیستم لحاظ شده است. همچنین توان 24 ولت براساس لیست بار ابزاردیق می باشد.
16-2 | Rated current of all outgoing shall be rechecked and modified. It seems some MCB rated current has not been selected correctly. For example The power consumption of feeder No. 2 for 110VDC (MV switchgear incoming A+coupler+outgoing on bus A) is 4491W and so the current is 41A. Meanwhile spare feeders shall be modified base on above mention comment. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17 | فیدر های خروجی تابلو های 24 ولت و 110 ولت به روز رسانی گردید.
16-3 | Power supply of F&G lighting panel lighting has been considered on 24VDC distribution panel. According to our previous agreement, it will be fed from emergency lighting panel and so shall be modified. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17
16-4 | FACP system base on instrument power consumption list will be fed by 24VDC distribution panel. So it shall be added to SLD. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17
16-5 | Outgoing cables size shall be rechecked and modified base on above mentioned comments and shall be finalized after finalizing cable list. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17 | بعد از تکمیل لیست کابل نهایی خواهد شد.
17 | Following item shall be added as notes: - Interlocks will be provided to active battery room ventilation when UPS is on battery boost charge mode. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17 | نوت شماره 3 , 4 نحوه ارتباط بین باتری های و فن و سیستم G&G را نشان می دهد.
18 | 24VDC battery capacity shall be modified base on latest revision of DC charger calculation document. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17 | براساس آخرین ویرایش مدرک محاسبات به روز رسانی گردید.
19 | one 110Vdc outgoing feeder shall be added for feeding RCP control circuits. |  | BK-SUR-ENG-ELE-01-05479 | 2022-08-17 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 17-Aug-22 |  |  |  |  | Date: