## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0026_D06 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1655 |  |  | Transmital Date: 17/Des/2022
Document Title: Mechanical Data Sheets for Diesel Pump |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-ME-TR-1655 |  |  | Transmital Date: 17/Des/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0026_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | از آنجا که تا کنون هیچ تاییدیه ای در خصوص این مدرک ارسال نشده است لذا انتشار آن با وضعیت AFC پذیرفتنی نیست. |  | 1401-2294-397528 | 1401/10/19 | با توجه به پاسخ اصلاحی پیوست کارفرمای محترم با شماره نامه 1401-2294-444182 مورخ 1401/11/20 : 1-مقتضی است، بند های 2،3 و 4 نامه شماره 397528 در خصوص اختصاص باتری و باتری شارژ 24VDCFH با توجه به موضوعیت نداشتن جهت پمپ های لودینگ سوخت دیزل پمپ، کان لم یکن تلفی گردند. 2. درخصوص موارد الکتریکال قید شده در مدرک نظر خاصی مطرح نیست .
2 | مطابق بند 6.11.3 استاندارد IPS-M-PM-2900-(2 میبایست تعداد 2 مجموعه باتری 20 عددی نیکل کادمیوم جهت استارتینگ دیزل پمپ لحاظ گردد. همچنین ظرفیت باتری های مذکور نباید از 200 آمپر ساعت کمتر باشد. در این راستا ضروری است محاسبات مربوط به ظرفیت باتری بر اساس توان موتور الکتریکی استارتر نیز ارائه شود. |  | 1401-2294-397528 | 1401/10/19
3 | شارژر میبایست بصورت دوگانه و ساختار آن بصورت تایر ستوری در نظر گرفته شود. |  | 1401-2294-397528 | 1401/10/19
4 | موارد برقی قید شده در داده برگ فنی شامل: 1و2و12و24و25 مربوط به پمپ با درایور الکتریکی است و ارتباطی با دیزل پمپ ندارد لذا می بایست حذف شود |  | 1401-2294-397528 | 1401/10/19
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: S.Zafaresmaeili | Signature | M.Fakharian
| Date: |  |  |  |  | Date: 06/JUN/2023