## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR FLOW TRANSMITTER /DIFF. PRESSURE TRANSMITTER- EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | DT | 0007 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR FLOW TRANSMITTER /DIFF. PRESSURE TRANSMITTER- EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | MAY.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D02 |  | SEP.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | DEC.2021 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-707977
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR FLOW TRANSMITTER /DIFF. PRESSURE TRANSMITTER- EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | DT | 0007 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X |  |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR FLOW TRANSMITTER /DIFF. PRESSURE TRANSMITTER- EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | DT |  | 0007 | D03
REFERENCE DOCUMENTS :
| Specification for Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| P&ID - Extension of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| Piping Material Specification | [6 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
| Instrument & Control System Design Criteria | [6 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
| Process Flow Diagram - Extension of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-PR-PF-0001

## Note
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR FLOW TRANSMITTER /DIFF. PRESSURE TRANSMITTER- EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0007 | D03
GENERAL NOTES:
1 - Zero and span adjustment shall be included and be accessible from outside in addition to HHC.
2 - Over range protection (at least 30% full scale) shall be considered. For differential pressure transmitters (including DP type flow transmitters), over range pressure protection shall be able to protect the sensing element from 1.3 times of the maximum design pressure applied to each side with the opposite side vented to atmosphere.
3 - S.S. name plate including project description to be provided.
4 - Painting shall be in accordance with manufacturer standard.
5 - VTA : Vendor To Advise
6 - N/A : Not Applicable
7- Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: -5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % (Note */ Note**) DB FOR Winter HVAC Design: 6 °C Note * * Refer to " HVAC Design Criteria; N.I.O.C. NO.: F-1-B-422001". ** Refer to “NISOC Meteorological Studies Report".
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
8 - Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.
9 - The manifold valves on Pressure and differential transmitters shall be bracket mounted type with the base bracket mounting holes such that the instruments can be directly connected to the manifold valves, and the assembly can be installed and supported on 2" stanchions by bracket mounted manifolds.

## FT
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR FLOW TRANSMITTER /DIFF. PRESSURE TRANSMITTER- EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  |  | BK | W007S | PEDCO | 110 | IN |  | DT | 0007 | D03
GENERAL DATA |  |  | 1 | Tag No. | [7 empty] | SEE NEXT PAGE
|  |  | 2 | P&ID No. | [7 empty] | SEE NEXT PAGE
|  |  | 3 | Equipment No. / Line No. | [7 empty] | SEE NEXT PAGE
|  |  | 4 | Area Classification | [7 empty] | ZONE 2, IIB T4
|  |  | 5 | Piping Class | [7 empty] | SEE NEXT PAGE
OPERATING CONDITIONS |  |  | 6 | Fluid | [7 empty] | SEE NEXT PAGE
|  |  | 7 | Phase | [7 empty] | SEE NEXT PAGE
|  |  | 8 | Operating Pressure | [5 empty] | (Barg) |  | SEE NEXT PAGE
|  |  | 9 | Design Pressure | [5 empty] | (Barg) |  | SEE NEXT PAGE
|  |  | 10 | Operating Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
|  |  | 11 | Design Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
|  |  | 12 | Min./Normal/Max Flow Rate | [5 empty] | (Kg/h) |  | SEE NEXT PAGE
TRANSMITTER |  |  | 13 | Element Type | [7 empty] | SEE NEXT PAGE
|  |  | 14 | Size of Process Connection | [7 empty] | SEE NEXT PAGE
|  |  | 15 | Rating of Process Connection | [7 empty] | -
|  |  | 16 | Element Material | [7 empty] | SEE NEXT PAGE
|  |  | 17 | Enclosure Material | [7 empty] | Die cast aluminium
|  |  | 18 | Instrument Range | [7 empty] | SEE NEXT PAGE
|  |  | 19 | Power Supply | [7 empty] | 24 VDC-Loop powered
|  |  | 20 | Output Signal | [7 empty] | 4-20mA
|  |  | 21 | Communication Protocol | [7 empty] | SMART HART (4-20mA)
|  |  | 22 | Electrical Connection | [7 empty] | ISO M20 x 1.5
|  |  | 23 | Electrical Certification | [7 empty] | EEx "ia"
|  |  | 24 | Weather Protection | [7 empty] | IP-65 as minimum
|  |  | 25 | Accuracy | [7 empty] | +/- 0.1% F.S
|  |  | 26 | Repetability | [7 empty] | +/- 0.1% or better
|  |  | 27 | Span and Zero Adjustment | [7 empty] | Required
|  |  | 28 | Over Range Protection | [7 empty] | SEE NEXT PAGE (1.3 of F.S)
DIAPHRAGM SEAL |  |  | 29 | Type | [7 empty] | N/A
|  |  | 30 | Size (In) | [7 empty] | N/A
|  |  | 31 | Fill Fluid | [7 empty] | N/A
|  |  | 32 | Diaphragm Material | [7 empty] | N/A
|  |  | 33 | Capillary Material | [7 empty] | N/A
|  |  | 34 | Capillary Length | [7 empty] | N/A
OPTIONS |  |  | 35 | Integral Indicator |  |  |  | Display Unit |  |  |  | Required |  |  | Barg
|  |  | 36 | Mounting Brackets |  |  |  | Material |  |  |  | Required, 2" Support Pipe (Note 9 in General Note) |  |  | VTA
|  |  | 37 | Manifold |  |  |  | Body Material |  |  |  | SEE NEXT PAGE |  |  | 316 S.S.L
|  |  | 38 | Connection | [7 empty] | 1/2 " NPT
|  |  | 39 | Manifold Model |  |  |  | Manifold Manufacturer |  |  |  | -
|  |  | 40 | Integral Indicator Style | [7 empty] | LCD TYPE
|  |  | 41 | NACE Requirements | [7 empty] | SEE NEXT PAGE
PURCHASING DATA |  |  | 42 | Model |  |  |  | Manufacturer |  |  |  | Will Be Finalized Later |  |  | Will Be Finalized Later
|  |  | 43 | Supplier |  |  |  | Order |  |  |  | Will Be Finalized Later |  |  | Will Be Finalized Later
| NOTES : | VTA : VENDOR TO ADVISE
N/A : NOT APPLICABLE
D03

## FT LIST
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR FLOW TRANSMITTER /DIFF. PRESSURE TRANSMITTER- EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  |  | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  |  |  | BK | W007S |  | PEDCO |  | 110 |  | IN |  |  | DT |  | 0007 |  | D03
PRESSURE TRANSMITTER
Rev. | Item No. | Tag No. | P&ID No. | Equipment No. / Line No. | Service | Fluid | Piping Class /Line Size | Phase | Design Pressure (Barg) | Operating Pressure (Barg) | Design Temp. (°C) | Operating Temp. (°C) | Calibration Range (mBarg) (Note 1) | Instrument Range | Flow Rate (Kg/h) |  |  | Element Type | Element Material | Size of Process Connection (Orifice Flange Tapping) | Over Range Protection (As Per Note 2 in General Notes) (Barg) | 5-Way Valve (1/2"NPTFx1/4"NPTF ) | NACE | Model | Remark
[15 empty] | Min. | Normal | Max.
D03 | 1 | FT-1701A | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) _ D04 | CRD-110-171A-FN05-4"-PT | FROM WELL NO. W018S | crude oil | 600# / 4" | 3 phase (Crude oil/Water/Vapour) | 93 | 12.78 | 85 | 36.31/22.62 | 0-250 | VTA | 3782.3447 | - | 11347.0341 | Diaphragm | SS 316L | 2 x 1/2" NPT | 120 | Yes | Yes | VTA
D03 | 2 | FT-1701B | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) _ D04 | CRD-110-171B-FN05-4"-PT | FROM WELL NO. W046S | crude oil | 600# / 4" | 3 phase (Crude oil/Water/Vapour) | 93 | 12.78 | 85 | 31.60/15.20 | 0-250 | VTA | 11614.6063 | - | 17421.9094 | Diaphragm | SS 316L | 2 x 1/2" NPT | 120 | Yes | Yes | VTA
D03 | 3 | FT-1701C | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) _ D04 | CRD-110-171C-FN05-4"-PT | FROM WELL NO. W008N | crude oil | 600# / 4" | 3 phase (Crude oil/Water/Vapour) | 93 | 12.78 | 85 | 46.19/33.90 | 0-250 | VTA | 3782.3447 | - | 11347.0341 | Diaphragm | SS 316L | 2 x 1/2" NPT | 120 | Yes | Yes | VTA
D03 | 4 | FT-1701D | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) _ D04 | CRD-110-171D-FN05-4"-PT | FROM WELL NO. W028 | crude oil | 600# / 4" | 3 phase (Crude oil/Water/Vapour) | 93 | 12.78 | 85 | 44.41/32.15 | 0-250 | VTA | 18147.8222 | - | 29036.5156 | Diaphragm | SS 316L | 2 x 1/2" NPT | 120 | Yes | Yes | VTA
D03 | 5 | FT-1701E | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) _ D04 | CRD-110-171E-FN05-4"-PT | FROM WELL NO. W035 | crude oil | 600# / 4" | 3 phase (Crude oil/Water/Vapour) | 93 | 12.78 | 85 | 40.71/27.31 | 0-250 | VTA | 18147.8222 | - | 29036.5156 | Diaphragm | SS 316L | 2 x 1/2" NPT | 120 | Yes | Yes | VTA
D03 | 6 | FT-1701F | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) _ D04 | CRD-110-171F-FN05-4"-PT | FROM WELL NO. W007S | crude oil | 600# / 4" | 3 phase (Crude oil/Water/Vapour) | 93 | 12.78 | 85 | 41.77/22.21 | 0-250 | VTA | 5807.3031 | - | 11614.6062 | Diaphragm | SS 316L | 2 x 1/2" NPT | 120 | Yes | Yes | VTA
D03