## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-CN-0002-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1934 |  |  | Transmital Date: 06-Mar-2023
Document Title: Calculation Note for UPS System - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0112-EL-TR-1934 |  |  | Transmital Date: 06-Mar-2023
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-CN-0002-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اینکه برآورد ارائه شده به صورت تقریبی می باشد، بررسی دقیق تر مدرک پس از ارائه پیشنهاد سازندگان انجام می گردد. |  | 1402-2290-13121 | 1402-01-18 | لیست بار ایزاردقیق در نظر گرفته شده برای انجام محاسبات، ترنسمیتال 1899 است که ملاک سایزینگ بخش برق می باشد. در صورت هر گونه تغییر در مدارک ابزاردقیق این مدرک ویرایش خواهد شد. همچنین سازنده موظف است آخرین مدارک محاسباتی را در هنگام خرید مد نظر قرار دهد.
2 | در صورتی که ظرفیت برآورد شده کمتر از ظرفیت اسناد پیمان باشد، ظرفیت موجود در اسناد پیمان ملاک عمل قرار خواهد گرفت. |  | 1402-2290-13121 | 1402-01-18 | ظرفیت اسناد پیمان 15 کیلووات است. در حالیکه در محاسبات این عدد کمی بیشتر از 14 کیلووات است. لذا مطابق با اسناد پیمان، عدد 15 کیلووات میبایست توسط وندور در نظر گرفته شود.
3 | لازم است، بر اساس ابعاد شارژر و باتری های پیشنهادی، مدارک چیدمان باتری ها به روزرسانی و جهت بررسی به این امور ارسال گردد، در صوریکه در جانمایی جدید، فضاهای موجود (توافق شده در صورتجلسه24-08-1401) جوابگو نباشد، میبایست تبعات مالی/زمانی انجام کار در قالب فرم C/R جهت طرح در کمیته تغییرات به کارفرما ارائه گردد. |  | 1402-2290-13121 | 1402-01-18 | براساس آخرین محاسبات، جانمایی شارژر و باتری های سیستم AC UPS , DC UPS جهت تایید برای آن کارفرمای محترم ارسال خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-Mar-23 |  |  |  |  | Date: