## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0003-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1949 |  |  | Transmital Date: 11-Mar-2023
Document Title: DC Charger Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0112-EL-TR-1949 |  |  | Transmital Date: 11-Mar-2023
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-SL-0003-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 14 در قسمت NOTES مورد تایید نیست، پیرو موارد مندرج در نامه شماره 448439 مورخ 1401/11/24، هر کدام از تابلو های ابزاردقیق می بایست به صورت مستقیم و Redundant از تابلوی توزیع اصلی سیستم UPS-110VAC و یا شارژر 24VDC تغذیه گردند، لذا جانمایی تابلو توزیع در اتاق کنترل مورد تایید این امور نمی باشد. |  | 1401-2294-5210 | 1402-01-08 | با توجه به وجود تعدادی فیدر بر روی تابلوی شارژر، و فاصله زیاد از اتاق UPS تا پنل های مارشالینگ در ساختمان کنترل، برای یکپارچگی در طراحی با ایستگاه، یک تابلوی DP در اتاق کنترل نصب خواهد شد که دو کابل یکی به صورت اصلی و یکی به صورت ریداندانت در نظر گرفته شده است که تابلوی DP را تغذیه می کند. در داخل تابلوی DP نیز برای هر فیدر خروجی یکی به صورت اصلی و یکی به صورت ریداندانت می باشد. که همه این موارد در مدرک دیاگرام تک خطی نمایش داده شده می شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 15-Mar-22 |  |  |  |  | Date: