## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0001_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1199 |  |  | Transmital Date: 26-Jul-2022
Document Title: Overall Single Line Diagram of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1199 |  |  | Transmital Date: 26-Jul-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-SL-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ردیف های 1 و 2 از برگ پاسخ، در مدرک اعمال نشده است.تأکید این امور جهات حفاظت خط انتقال، استفاده از ترکیب کات اوت فیوز به همراه LBS و ارت سوییچ در محل انشعابات می باشد. در طراحی فعلی در صوئرتیکهدر مسیر خط هوایی پروژه اتصالی رخ دهد این خطا موجب عملکرد فیدرهای بالادست F2 و F15 در کلیدخانه تراکم گاز و در نتیجه باعث بی برقی خط و باعث توقف واحدهای تولیدی خواهد شد. لذا نصب فیوز در محل انشعابات بر اساس بند 7.5.8.4 Tee of Protection استاندارد 100 الزامی است. لذا مدارک بر این اساس می بایست اطلاح گردند. |  | 1401-2294-217200 | 1401-06-19 | پیرو مذاكرات صورت گرفته و همچنین صورتجلسه مورخ 1401/08/24 در محل سالن جلسات کمپ بینک؛ اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 09-Aug-22 |  |  |  |  | Date: