## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-W007S-PEDCO-110-IN-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-NISOC-T-1398 |  |  | Transmital Date: 13 Sep 2022
Document Title: Control Room Cable Route Layout - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1398 |  |  | Transmital Date: 13 Sep 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به تغییر کاربری اتاق باطری شارژر، مدرک نیاز به بازنگری مجدد دارد. |  | 1401/2294/279765 | 1401/08/03 | مدرک اصلاح گردید.
2 | حداکثر دولایه کابل فشار ضعیف در تراشه کابل در نظر گرفته شود. |  | 1401/2294/279765 | 1401/08/03 | ملاحظه گردید.
3 | کابل های کنترل بصورت یک لایه در بالای کابل های فشار ضعیف با فاصله 300 میلی متر توسط سینی اجرا گردد. |  | 1401/2294/279765 | 1401/08/03 | مدرک اصلاح گردید.
3 | در مسیر های عمودی جهت حفاظت مکانیکی کابل از سینی استفاده گردد. |  | 1401/2294/279765 | 1401/08/03 | مسیر عمودی برای عبور کابل در اتاق کنترل وجود ندارد .
3 | با توجه به تعداد کابل های مجاور هم، در محاسبات سایزینگ کابل ها ضریب همگروهی مد نظر قرار گیرد. |  | 1401/2294/279765 | 1401/08/03 | سایز کابل های ابزاردقیق طبق مدرک " Specification For Instrument/F&G Cables" به سایز های 1،1.5 و 2.5 میلیمتر مربع می باشد . لازم به ذکر است محاسبات سایزینگ برای کابل های بخش برق می باشد.
3 | ملزومات ذکر شده در استاندارد IPS-E-EL-100 در مدارک مورد توجه قرار گیرد. |  | 1401/2294/279765 | 1401/08/03 | مدرک بر اساس استانداردهای Low Voltage تهیه شده است از جمله استاندارد IPS-M-EL-271 ، IPS-E-IN-190و IPS-C-IN-190 تهیه شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 26 Sep 2022 |  |  |  |  | Date: