## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-EL-LI-0002_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1513 |  |  | Transmital Date: 18-Oct-2022
Document Title: Electrical power & control cable list in siahmakan gas injection |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1513 |  |  | Transmital Date: 18-Oct-2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-EL-LI-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | It shall be revised after finalizing or minor comments on electrical load list in siahmakan gas injection. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | بیشترین توان بار برای این ترانس یعنی 15 کیلووات در نظر گرفته شده است. در صورت انجام محاسبه نهایی، این عدد مورد ویرایش قرار خواهد گرفت. |  |  | See below item 7.
2 | Cable type shall be completely mentioned in cable list such as conductor type, inner and outer insulation (XPLE or PVC), armour, Screen, etc in legend sheet. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | نوع کابل به صورت CU/XLPE/SWA/PVC در نظر گرفته شده است. |  |  | Noted and Closed.
3 | Gland type(Ex or Non-ex) and size shall be specified. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | مشخص گردید. |  |  | Noted and Closed.
4 | According to scope of work, cable length shall be rechecked and modified (if required). |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | طول کابل مشخص گردید. |  |  | See below item 8.
5 | Reference document for OD cables and gland size shall be attached to document and submitted in next revision to check OD cables and gland size. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | مرجع کابل ابهر می باشد. که پیوست می گردد. |  |  | Noted and Closed.
6 | Tag number of cable shall be modified according to cable tag numbering procedure in legend sheet. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | تگ نامبر کابل حذف گردید. |  |  | Noted and Closed.
7 | See above item 1: According to our telephone conversation, cathodic protection calculation has not been revised. This document shall be submitted after finalizing or minor comments on cathodic protection calculation. |  | BK-SUR-ENG-ELE-01-06041 | 2022-10-31 | مطابق با شرح کار پروژه، برقرسانی به حفاظت کاتدیک از طریق فیدر 63 آمپر به شماره L11 خواهد بود. لذا بر اساس محاسبات اولیه توان مورد نیاز سیستم کاتدی 15 کیلووات در نظر گرفته شده است که منطقی می باشد. با این حال در صورتیکه توان این سیستم بعد از محاسبات بیشتر بود، مدرک لیست کابل به روزرسانی خواهد شد.
8 | See above item 4: See attached file and it shall be clarify while the area electrical cable route & section layout in Siahmakan Gas Injection has not been submitted. |  | BK-SUR-ENG-ELE-01-06041 | 2022-10-31 | مطابق با شرح کار پروژه، برقرسانی به حفاظت کاتدیک از طریق فیدر 63 آمپر به شماره L11 خواهد بود. این موضوع در مدرک نشان داده شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Oct-2022 |  |  |  |  | Date: