## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-LI-0001-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1429 |  |  | Transmital Date: 21-Sep-2022
Document Title: Electrical Load List - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1429 |  |  | Transmital Date: 21-Sep-2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-LI-0001-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت محاسبه توان شارژر و در نتیجه محاسبه لیست بار، می بایست از ولتاژ Boost باتری(1.65 ولت جهت هر سلول، پیرو نامه شماره 320825 مورخ 1400/09/26) و راندمان سیستم استفاده شود، بدین ترتیب بار ورودی شارژر به 4.6kw و بار ورودی دستگاه UPS به 20KW افزایش می یابد، در همین ارتباط ضروری است، مدارک مرتبط از جمله مدرک تک خطی سوئیچگیر توسعه یافته کلاستر نیز اصلاح گردد. |  | 1401-2294-279683 | 1401-08-03 | مطابق با محاسبات جدید انجام شده که با ترنسمیتال 2158 , 2155 ارسال شده است، توان های جدید برای هر دو سیستم UPS و DC Charger به ترتیب 14.3 و 16.39 است. ولی از آنجا که کارفرمای محترم تأکید داشته که اعداد اسناد پیمان ملاک باشد، عدد 15 کیلووات برای UPS در نظر گرفته شده است. همچنین برای DC UPS 16.39 کیلووات در نظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Otc-22 |  |  |  |  | Date: