## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-BK-W007S-PEDCO-110-AR-DW-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-TR-0885 |  |  | Transmital Date:01/MAY/2022
Document Title: Architectural Drawing For Diesel Generator Shelter of Well Pads - BK-W007S |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-AR-TR-0885 |  |  | Transmital Date: 01/MAY/2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-GCS-PEDCO-110-AR-DW-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مساحت طراحی شده برای این سایبان نسبت به اسناد پیمان (در حدود 12 متر مربع) دارای کاهش است.مبنای ابعاد مدل سازی، توضیح داده شود.متذکر می گردد مساحت سازه باید به گونه ای تعیین گردد،که الزامات بخش مکانیک،برق و ایمنی را در برگیرد. |  | 1401-2294-55003 | 1401/02/19 | اعمال شد.
2 | محل ورودی ترنچ به این سازه مبهم می باشد.مقتضی است SECTION B در راستای محورB قرار داده شده و جزئیات کامل آن نمایش داده شود. |  | 1401-2294-55003 | 1401/02/19 | اعمال شد.
3 | ELEVATION 2 دارای اشکالات ترسیمی است،برای مثال ترنچ ورودی به همراه ترازهای متعلق به آن (ورودی و خروجی) سایبان،دیده نمی شود،اصلاح گردد. |  | 1401-2294-55003 | 1401/02/19 | اعمال شد.
4 | باتوجه به اینکه تیپ تجهیز مربوطه تاکنون نهایی نشده،مقتضی است تمهیدات لازم در خصوص خروجی لوله یEXHAUST، از سقف یا کناره،در نظر گرفته شود. |  | 1401-2294-55003 | 1401/02/19 | اعمال شد.
5 | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
6
7 | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
8 | Commented By: | Signature |  |  |  | Clarified By: | Signature
9
10 | Date: |  |  |  |  | Date:
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
Legend
Signature