## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-PY-0004_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1749 |  |  | Transmital Date: 01-Jan-2023
Document Title: Lighting & Small Power Layout For Switchgear Building of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-EL-TR-1749 |  |  | Transmital Date: 01-Jan-2023
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-PY-0004_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | تعداد 2 عدد پریز در کلید خانه اضافه شود. |  | 01-2294-419775 | 1401-11-03 | اعمال گردید.
2 | بالای درب نفر رو در کلید خانه EXIT LIGHT اضافه شود. |  | 01-2294-419775 | 1401-11-03 | اعمال گردید.
3 | یک عدد چراغ بر روی دیوار ضلع پشتی کلید خانه مجاور شلتر ترانس اضافه شود. |  | 01-2294-419775 | 1401-11-03 | اعمال گردید.
4 | براساس نقطه نظراتی دریافتی از اداره تعمیرات گچساران به جهت سهولت تعمیرات سیستم روشنایی، پیشمهاد می شود، چراغ های اطراف کلید خانه و چراغ های شلتر ترانس با چراغ های فلورسنت 1x36w جایگزین گردند. |  | 01-2294-419775 | 1401-11-03 | اعمال گردید.
5 | چراغ های درون اتاق باتری به جهت پخش نور بهتر در سقف اتاق نصب گردند. |  | 01-2294-419775 | 1401-11-03 | اعمال گردید.
6 | سیستم تهویه(کولر اسپلیت) اتاق باتری نمایش داده نشده است. |  | 01-2294-419775 | 1401-11-03 | در صورت نهایی سازی سیستم HVAC، سوکت کولر اسپلیت در نظر گرفته خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 16-Jan-23 |  |  |  |  | Date: