## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0002_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1749 |  |  | Transmital Date: 01-Jan-2023
Document Title: Calculation Note For Lighting System of Well Pads Switchgear Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-EL-TR-1749 |  |  | Transmital Date: 01-Jan-2023
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0002_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on architectural drawing for switchgear building of well pads . |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | مدرک مطابق با آخرین ویرایش مدرک معماری (ترنسمیتال شماره 1370) اصلاح گردید و در صورت هر گونه تغییر این مدرک ویرایش خواهد شد. |  |  | Noted and Closed.
2 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22
2-1 | A separat table shall be added to this document and shall be compared calculated Lux with IPS-E-EL-100 standard to check the result of calculation. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | متن مربوط به مقایسه جدول استاندارد و محاسبات روشنایی اضافه گردید. |  |  | Noted and Closed.
2-2 | The calculation shall be rechecked and modified from point of view the dimensions of the rooms and value of standard lux for example for switchgear room. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | همانطور که در پاسه شماره یک عنوان گردید، با توجه به تغییر معماری ساختمان، این مدرک به روز رسانی و ابعاد جدید لحاظ شد. |  |  | Noted and Closed.
3 | Workplane/Value Chart shall be added to output reports for each room to check Emin/Emax. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | بررسی و تمامی نقشه های مورد نیاز اضافه گردید. |  |  | Noted and Closed.
4 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-04347 | 2022-05-22 | در صورت وجود هر گونه کامنت احتمالی، تغییرات متعاقبا لحاظ خواهد شد. |  |  | Noted and Closed.
5 | No Comment. Note: According to our telephone conversation, the height of rooms and mounting height shall be modified base on latest revision of architectural drawing For switchgear building of Well Pads. |  | BK-SUR-ENG-ELE-01-05982 | 2022-10-26 | مطابق با آخرین ویرایش مدرک معماری اصلاح گردید. |  |  | Noted and Closed.
6 | No Comment. Note: If any changes in prerequisite documents such as architectural drawing for switchgear building of well pads or after receiving NISOC comments that affects on document, this document shall be updated and submitted again. |  | BK-SUR-ENG-ELE-01-06654 | 2023-01-16 | هر گونه تغییر آینده اعمال خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 16-Jan-23 |  |  |  |  | Date: