## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0035_D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1373 |  |  | Transmital Date: 07/Sep/2022
Document Title: Mechanical Data Sheets for Glycol Drain Pump |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-1373 |  |  | Transmital Date: 07/Sep/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0035_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | میزان اختلاف فشار ذکر شده با آخرین ویرایش مدرک P&ID همخوانی ندارد ضروریست یکسان سازی گردد. همچنین Tag.No. ذکر شده با مدرک P&ID مطابقت ندارد. |  | 1401/2294/325671 | 1401/09/02 | با توجه به تغییر ارتفاع مخزن، میزان فشار خروجی و Diff. Pressure مطابق آخرین ویرایش مدرک P&ID اصلاح می گردد.همچنین Tag.No. مطابقت داده شد.
2 | مشخص گردد مقدار Plant NPSH چگونه محاسبه شده و در مدرک درج شده است. |  | 1401/2294/325671 | 1401/09/02 | مبنای درج Plant NPSH (NPSHA) مدرک محاسبات و دیتاشیت فرآیندی می باشد که مطابق با آخرین تغییرات این مدارک (که توسط بخش فرآیند برای کارفرمای محترم ارسال خواهد شد) مقدار NPSHA در مدرک مکانیکال اصلاح می گردد.
3 | مبنای محاسبه فشار ورودی پمپ مشخص گردد. |  | 1401/2294/325671 | 1401/09/02 | مبنای درج فشار ورودی پمپ مدرک فرآیندی مربوطه بوده که مطابق آخرین تغییرات این مدارک 0.11برای حداقل و 0.20 برای حداکثر فشار ورودی تعیین شده است.
4 | سایز و کلاس فلنج خروجی اصلاح گردد. |  | 1401/2294/325671 | 1401/09/02 | مطابق استاندارد IPS-M-PM-115 ، کلاس فلنج های ورودی و خروجی پمپ های یک و دو طبقه می بایست یکسان باشد. همچنین مطابق مدرک P&ID سایز خطوط ورودی و خروجی پمپ 2 اینچ بوده که در نوت شماره 14 به آن اشاره و بخش مربوطه در دیتاشیت نیز اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: S.Zafaresmaeili | Signature | M.Fakharian
| Date: |  |  |  |  | Date: 13/JUN/2023