## TOTAL
DC Charger & Batteries Sizing Calculation
Panel Tag | P1 | P2 |  | P3 |  | P4
LV Switchgear of Wells | 858 | 258 |  | 1458 |  | 858
Total | 858 | 258 |  | 1458 |  | 858
Total considering 20% Growth Factor | 1029.6 | 309.6 |  | 1749.6 |  | 1029.6
P/2 for Batt. Sizing | 514.8 | 154.8 |  | 874.8 |  | 514.8
Note: Simultaneous factor of 0.8 is considered for closing coil & motor charger consumptions at interval P3.
|  |  | Period | Total Power (W) | Duration (sec) |  | Section Size (sec)
|  |  | 1 | 514.8 | 60 |  | 60
|  |  | 2 | 154.8 | 28620 |  | 28680
|  |  | 3 | 874.8 | 60 |  | 28740
|  |  | 4 | 514.8 | 60 |  | 28800
[8 empty] | 0.001 | 514.8
[8 empty] | 60 | 514.8
[8 empty] | 60 | 154.8
[8 empty] | 28680 | 154.8
[8 empty] | 28680 | 874.8
[8 empty] | 28740 | 874.8
[8 empty] | 28740 | 514.8
[8 empty] | 28800 | 514.8
[8 empty] | 28800 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0

## 400-NSWG-001
110 VDC LOAD FOR DC -UPS-01
NO | DESCRIPTION | NO. OF SETs | POWER CONSUMPTION OF EACH FEEDER |  |  |  | TOTAL POWER CONSUMPTION OF SWICHGEAR |  |  | DC LOAD PERIOD (IEEE Std 1115-2000) |  |  |  | REMARKS
|  |  | QUANTITY | RATED POWER (W) | UTL FACTOR | Power demand (W) | NO OF FEEDERS | UTL FACTOR | TOTAL POWER (W)
[10 empty] | p1 | p2 | p3 | p4
1 | INCOMING FEEDERS | 3
1.1 | CB SPRING CHARGING MOTOR |  | 1 | 200 | 1 | 200 |  | 1 | 600 | 0 | 0 | 1 | 0
1.2 | ACB CLOSING COIL |  | 1 | 200 | 1 | 200 |  | 1 | 600 | 0 | 0 | 1 | 0
1.3 | ACB SHUNT RELEASE |  | 1 | 200 | 1 | 200 |  | 1 | 600 | 1 | 0 | 0 | 1
1.4 | ACB UNDER VOLTAGE COIL |  | 1 | 5 | 1 | 5 |  | 1 | 15 | 1 | 1 | 1 | 1
1.5 | DIGITAL MULTIMETER |  | 1 | 3 | 1 | 3 |  | 1 | 9 | 1 | 1 | 1 | 1
1.6 | ALARM WINDOW |  | 1 | 3 | 1 | 3 |  | 1 | 9 | 1 | 1 | 1 | 1
1.7 | RELAY TCS ANSI CODE 74 |  | 1 | 3 | 1 | 3 |  | 1 | 9 | 1 | 1 | 1 | 1
1.8 | RELAY FOR LOCK OUT ANSI CODE 86 |  | 1 | 3 | 1 | 3 |  | 1 | 9 | 1 | 1 | 1 | 1
1.9 | AUX. RELAYS |  | 10 | 3 | 0.7 | 21 |  | 1 | 63 | 1 | 1 | 1 | 1
1.10 | SIGNAL LAMPS |  | 10 | 3 | 0.7 | 21 |  | 1 | 63 | 1 | 1 | 1 | 1
1.11 | MULTIFUNCTION PROTECTION RELAY |  | 1 | 27 | 1 | 27 |  | 1 | 81 | 1 | 1 | 1 | 1
2 | BUS SECTION FEEDER | 0
2.1 | CB SPRING CHARGING MOTOR |  | - | - | - | - |  | - | - | - | - | - | - | BECAUSE OF 2/3 LOGIC
2.2 | ACB CLOSING COIL |  | - | - | - | - |  | - | - | - | - | - | - | BECAUSE OF 2/3 LOGIC
2.3 | ACB SHUNT RELEASE |  | - | - | - | - |  | - | - | - | - | - | - | BECAUSE OF 2/3 LOGIC
2.4 | ACB UNDER VOLTAGE COIL |  | 1 | 5 | 1 | 5 |  | 1 | 0 | 1 | 1 | 1 | 1
2.5 | RELAY TCS ANSI CODE 74 |  | 1 | 2.5 | 1 | 2.5 |  | 1 | 0 | 1 | 1 | 1 | 1
2.6 | RELAY FOR LOCK OUT ANSI CODE 86 |  | 1 | 2.5 | 1 | 2.5 |  | 1 | 0 | 1 | 1 | 1 | 1
2.7 | SYNCHRO CHECK RELAY |  | 1 | 6 | 1 | 6 |  | 1 | 0 | 1 | 1 | 1 | 1
2.8 | AUX. RELAYS |  | 10 | 3.5 | 0.7 | 24.5 |  | 1 | 0 | 1 | 1 | 1 | 1
2.9 | SIGNAL LAMPS |  | 10 | 2 | 0.7 | 14 |  | 1 | 0 | 1 | 1 | 1 | 1
2.10 | MULTIFUNCTION PROTECTION RELAY |  | 1 | 16 | 1 | 16 |  | 1 | 0 | 1 | 1 | 1 | 1
2.11 | DC UNDER VOLTAGE RELAY |  | 2 | 3.5 | 1 | 7 |  | 1 | 0 | 1 | 1 | 1 | 1
3 | OUTGOING FEEDER , CB OPERATED | 0
3.1 | CB SPRING CHARGING MOTOR |  | 1 | 200 | 1 | 200 |  | 1 | 0 | 0 | 0 | 1 | 0
3.2 | ACB CLOSING COIL |  | 1 | 200 | 1 | 200 |  | 1 | 0 | 0 | 0 | 1 | 0
3.3 | ACB SHUNT RELEASE |  | 1 | 200 | 1 | 200 |  | 1 | 0 | 1 | 0 | 0 | 1
3.4 | ACB UNDER VOLTAGE COIL |  | 1 | 5 | 1 | 5 |  | 1 | 0 | 1 | 1 | 1 | 1
3.5 | RELAY TCS ANSI CODE 74 |  | 1 | 5 | 1 | 5 |  | 1 | 0 | 1 | 1 | 1 | 1
3.6 | RELAY FOR LOCK OUT ANSI CODE 86 |  | 1 | 2.5 | 1 | 2.5 |  | 1 | 0 | 1 | 1 | 1 | 1
3.7 | AUX. RELAYS |  | 10 | 3.5 | 0.7 | 24.5 |  | 1 | 0 | 1 | 1 | 1 | 1
3.8 | SIGNAL LAMPS |  | 10 | 2 | 0.7 | 14 |  | 1 | 0 | 1 | 1 | 1 | 1
3.9 | MULTIFUNCTION PROTECTION RELAY |  | 1 | 11 | 1 | 11 |  | 1 | 0 | 1 | 1 | 1 | 1
|  |  |  | Total of the period (W) | [5 empty] | 858 | 258 | 1458 | 858
320
|  |  | Period | Total Power (W) | Duration (sec) |  | Section Size (sec) | [7 empty] | 0.001 | 858
|  |  | 1 | 858 | 60 |  | 60 |  |  | 28800 |  |  |  |  | 60 | 858
|  |  | 2 | 258 | 28620 |  | 28680 |  |  | 28860 |  |  |  |  | 60 | 258
|  |  | 3 | 1458 | 60 |  | 28740 |  |  | 28920 |  |  |  |  | 28680 | 258
|  |  | 4 | 858 | 60 |  | 28800 | [7 empty] | 28680 | 1458
[15 empty] | 28740 | 1458
[15 empty] | 28740 | 858
[15 empty] | 28800 | 858
[15 empty] | 28800 | 0.001
|  |  | Power |  |  |  | DC Load Profile diagram
S3
S2
S1
|  |  |  | p1 |  |  | p2 |  |  | p3
L1 | Base power
L2 | Starting power demand
L3 | Ending power demand |  |  | L2 | [5 empty] | L3
L1
Time (min)
120
| Period |  | Loads | Total Amper | Duration (min) | Section Size (Min)
| 1 |  | 1 | 100 | 10 | 28836.2
| 2 |  | 1 | 80 | 10 | 28846.2
| 3 |  | 1 | 60 | 10 | 28856.2
| 4 |  | 1 | 40 | 10 | 28866.2
| 5 |  | 1 | 20 | 10 | 28876.2
| 6 |  | 0 | 0 | 0 | 28876.2
| 7 |  | 0 | 0 | 0 | 28876.2
| 8 |  | 0 | 0 | 0 | 28876.2