## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0991 |  |  | Transmital Date: 23 May 2022
Document Title: Control Room Cable Route Layout |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0991 |  |  | Transmital Date: 23 May 2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به نامه 92236 مورخ 1401/03/17 این امور با موضوع جمع بندی نظرات در خصوص معماری اتاق کنترل اعلان می گردد. پس از انجام تغییرات جمع بندی شده این مدرک مجددا برای بررسی ارسال گردد. |  | '1401-2294-139947 | 1401/04/23 | ملاحظه گردید
2 | مسیر کابل های برق ساختمان نمایش داده شود |  | 1401-2294-139947 | 1401/04/23 | کابل های برق مربوط به تابلوها در پایین ترین سطح مطابق " DETAIL "A کابل کشی می شوند
3 | ترانشه های کابل برق و ابزار دقیق مطابق استاندارد IPS از همدیگر مجزا باشند |  | 1401-2294-139947 | 1401/04/23 | مطابق استاندارد IPS کابل های برق و ابزاردقیق مجزا و حداقل 30 سانتی متر می باشند
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 6 Jun 2022 |  |  |  |  | Date: