## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0991 |  |  | Transmital Date: 23 May 2022
Document Title: Control Room Cable Route Layout |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0991 |  |  | Transmital Date: 23 May 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اينكه مدارك پيش نياز مانند Arrangement اتاق كنترل نهايي نيست. در صورت هر گونه تغيير در اين مدرك منعكس شود. |  | BK-SUR-ENG-INS-01-04585 | 2022-05-23 | ملاحظه گردید
2 | F&G Cable route براي تمامي اتاق ها مشخص شود. |  | BK-SUR-ENG-INS-01-04585 | 2022-05-23 | پس از نهای شدن جانمای دتکتورهای تمامی اتاق ها مسیر آنها در مدرک اضافه خواهد شد
3 | مشخص گردد كه فاصله كافي بين كابل هاي ابزاردقيق و برق وجود دارد. |  | BK-SUR-ENG-INS-01-04585 | 2022-05-23 | کابل های برق در LADDER مربو ط به خود کابل کشی می شوند و از کابل های ابزاردقیق حداقل 30 سانتی متر فاصله دارند
4 | منظور از route مشخص شود. با توجه به اينكه كابل ها با واسط مشخص مانند Tray، Ladder و Conduit و … انتقال پيدا كند. در خصوص Route و Legend مربوطه شفاف سازي گردد. |  | BK-SUR-ENG-INS-01-04585 | 2022-05-23 | Legend مربوط به route و ladder , tray در مدرک نشان داده شده است.
5 | بازگشت به كامنت قبل، ارتباط قبل از Openning در ورودي اتاق كنترل مشخص گردد و همچنين ارتباط بين مسير كابل ها در اتاق UPS شفاف سازي شود. |  | BK-SUR-ENG-INS-01-04585 | 2022-05-23 | ارتباط قبل از opening ورودی اتاق کنترل در مدرک Instrument/F&G Cable Trench/Route Layout Drawing نشان داده شده است. در مدرک حاضر مسیر کابل کشی در اتاق ups نشان داده شده است.
6 | در خصوص جداسازي كابل هاي كنترلي F&G و ESD شفاف سازي گردد. |  | BK-SUR-ENG-INS-01-04585 | 2022-05-23 | کابل های F&G و ESD باتوجه به ماهیت مشابه در کنار هم می توانند کابل کشی شوند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 6 Jun 2022 |  |  |  |  | Date: