## CRS
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-ME-DT-0002_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1571 |  |  | Transmital Date: 02/Nov/2022
Document Title: DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-ME-TR-1571 |  |  | Transmital Date: 02/Nov/2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-ME-DT-0002_D04 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | درخصوص مدرک فوق مطابق جدول(16-4-3-5)"ب" (حداقل مقدار جریان و فشار آب در پشت شیرهای لوازم بهداشتی)مبحث 16 مقررات ملی ساختمان نفت ضروریست در محاسبات ارتفاع مخزن آب موارد دیگر جهت مصرف نیز در نظر گرفته شده و همچنین مطابق جدول مذکور بیشترین فشار جهت فشار پشت شیر مصرف کننده لحاظ گردد. |  | 01/2294/380841 | 1401/10/10 | با توجه به شرایط جدید مخزن به لحاظ تغییر ارتفاع و متریال، کلیه نقطه نظرات کارفرمای محترم مرتفع گردید.
2 | در محاسبات ارسالی فاصله از خروجی مخزن تا دورترین شیر مصرف کننده در نظر گرفته نشده است. |  | 01/2294/380841 | 1401/10/10
3 | فشار بارومتریک مطابق مدرک Design Basic لحاظ گردد. |  | 1401/2294/380841 | 1401/10/10
4 | جزییات نحوه اتصال سایبان به مخزن غیر فلزی در شماتیک ترسیمی در صفحه 6 مدرک نشان داده نشده است |  | 01/2294/380841 | 1401/10/10
5 | باتوجه به در معرض آفتاب بودن و ارتفاع مخزن و با در نظر گرفتن عمر طزاحی 25 ساله، استفاده از جنس غیر فلزی مورد ایید نیست. |  | 01/2294/380841 | 1401/10/10
توجه: با توجه به "Approved As Note" شدن مدرک در ویرایش قبلی و ارائه توضیحات تکمیلی و انجام اصلاحیه جزئی، مدرک با وضعیت AFC ارسال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H.Ghadyani | Signature | M.Fakharian
| Date: |  |  |  |  | Date: