## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-LI-0002_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1893 |  |  | Transmital Date: 21-Feb-2023
Document Title: I/O List For Control /ESD System |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1893 |  |  | Transmital Date: 21-Feb-2023
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-IN-LI-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه 6 ، نوت دو به درستی اصلاح گردد : سیگنال های کنترل و توقف ، مربوط به بسته کاری خطوط لوله 4 و 8 اینچ به سیستم کنترل و توقف جدید متصل شود ؛ تجهیزات توقف / کنترلی جدید در پنل موجود تنها نصب می شوند.(سیستم کنترل/توقف جدید مستقل از سیستم کنترل / توقف ایستگاه سیاهمکان بوده ، فقط یک سیگنال توقف کلی از سیستم موجود دریافت میکند.) |  | 1402/2294/2478 | 1402/01/06 | سیگنال های مرتبط با خط لوله 8 اینچ در قسمت لانچر (ایستگاه تقویت فشار) به سیستم کنترل و ESD جدید در این ایستگاه ، متصل میشوند تنها سیگنال های باقی مانده در قسمت ریسیور خط لوله در ایستگاه سیاهمکان با فرمان باز بسته شده نرمال و اضطراری شیر ESDV همچنین وضعیت آن شیر بوده که به ادوات جدید نصب شده در پانل کنترل / اضطراری موجود سیاهمکان متصل میشود. مطابق صورتجلسه 1402/03/22 جلسه اهواز با حضور نمایندگان هیرگان انرژی، پترو ایران و کارفرمای محترم سیگنال توقف اضطراری از سمت ایستگاه به این شیر ارسال نمیشود زیرا در صورت قطع سیستم سیاهمکان همچنان ارسال گاز از طریق خط لوله انجام می پذیرد. با توجه به موارد ذکر شده مدرک باز بینی شده است و ارسال گردید. ( لازم به ذکر است بر روی خط لوله ۴ اینچ ادوات ابزار دقیقی نصب نمیشود.)
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: