## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-BD-0001_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1238 |  |  | Transmital Date: 3 Aug 2022
Document Title: Block Diagram Configuration For Control/ESD/F&G System |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1238 |  |  | Transmital Date: 3 Aug 2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-IN-BD-0001_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-05468 | 2022-08-16 | ملاحظه گردید
2 | Note-6 مشخص شود. |  | BK-SUR-ENG-INS-01-05468 | 2022-08-16 | مطابق نظر کارفرما JB مشترک استفاده نمیشود لذا نوت حذف شده است.
3 | با توجه به توضيحات ارائه شده براي سيستم كنترل و قطع اضطراري سياهمكان، مشخص شود كه كدام سيگنال به سيستم كنترل سياهمكان و كدام سيگنال به سيستم قطع اضطراري سياهمكان متصل است. |  | BK-SUR-ENG-INS-01-05468 | 2022-08-16 | مطابق توافقات انجام شده هیچ سیگنالی با سیستم موجود سیاهمکان رد و بدل نمی شود و عملکرد خط لوله کاملا مستقل است . لوپ های جدید مربوط به قطع اضطراری و کنترل نرمال درپانل موجود سیاهمکان نصب میشود . عملکرد آن به لحاظ کنترل و ایمنی در مدرک نشان داده شده است.
4
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 16 Aug 2022 |  |  |  |  | Date: