## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DG-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1080 |  |  | Transmital Date: 15 Jun 2022
Document Title: Instrument Hook-up Diagram |  |  |  |  | PEDCO Tr. No.: |  |  | Transmital Date: 15 Jun 2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-IN-DG-0002_D00 |  |  | CRS Status: | C3
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به بند 13 قرارداد و نوع مدرك مسئوليت تعداد و نوع تجهيزات به كار رفته از نظر مالي و زماني بر عهده پيمانكار (هيرگان) مي باشد. |  |  | 2022-07-25 | ملاحظه گردید
2 | با توجه به Note -1 در خصوص PT ها متريال مربوطه به Manifold، U-Bolt و .... بايد بر اساس مدارك spec و PMS پروژه باشد. |  |  | 2022-07-25 | متریال در مدرکDATA SHEET مطابق با SPEC مشخص شده است
3 | با توجه به تغييرات ارائه شده در جلسه HAZOP/SIL/HAZID موارد مجددا بررسي و ارسال گردد. |  |  | 2022-07-25 | موارد مطابق گزارشات مطروحه و P&ID بازبینی و اصلاح شد
3 | براي CC ها المان اندازه گيري تا انتهاي خط لوله در نظر گرفته شود. |  |  | 2022-07-25 | با توجه به اینکه سرویس این خط گاز می باشد اندازه گیری در وسط خط مناسب می باشد
3 | موارد بخش پايپينگ به پيوست ارسال مي گردد. |  |  | 2022-07-25 | پیوست گردید
3 | نقطه نظرات بخش فرآيند متعاقبا ارسال مي گردد. |  |  | 2022-07-25 | ملاحظه گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Abari | Signature |  |  |  | Clarified By: | Signature
| Date: 25 Jul 2022 |  |  |  |  | Date: