## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-LD-0001_D00 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-T-1110 |  |  | Transmital Date: 22 Jun 2022
Document Title: Control System/ESD Logic Diagram |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1110 |  |  | Transmital Date: 22 Jun 2022
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-IN-LD-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه توضیح علائم و اختصارات در نظر گرفته شود |  | 01/2294/213331 | 1401/06/15 | با توجه به نظر کارفرمای محترم اعمال گردید
2 | توضیح NOTE ها صحیح نمی باشد، تجهیزات توقف و کنترلی جدید در پنل موجود نصب میشوند.سیگنال های کنترلی و ESD بایستی مجزا در نظر گرفته شوند و با توجه به این موضوع کل مدرک مورد باز نگری قرار گیرد |  | 01/2294/213331 | 1401/06/15 | با توجه به نظر کارفرمای محترم اعمال گردید
3 | حالت های SELECTOR SWITCH مشخص نمی باشد آیا فقط برای بستن شیر کاربرد دارد ؟ |  | 01/2294/213331 | 1401/06/15 | با توجه به نظر کارفرمای محترم در مدرک شفاف سازی گردید.
4 | برای مدرک منطقی مشاهده نمی شود و بصورت دیاگرام دیده میشود ، منطق لاجیک مدرک به وضوح مشخص گردد یا توضیح داده شود. |  | 01/2294/213331 | 1401/06/15 | هیچ INTERLOCK یا منطقی در این لوپ ها وجود ندارد و کاملا به صورت مستقیم از PUSH BOTTON فرمان ارسال و در لوپ ها نمایش داده میشود.
5 | بین LIMIT SWITCH ها و لامپ ها نشان دهنده رله واسط در نظر گرفته شود. |  | 01/2294/213331 | 1401/06/15 | با توجه به نظر کارفرمای محترم اعمال گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: