## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For Temperature Transmitter/Switch
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0005 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
Data Sheets For Temperature Transmitter/Switch نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  |  | JUN.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  |  | NOV.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | MAR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F9Z-708926
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For Temperature Transmitter/Switch
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0005 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 |  | X | X | [5 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For Temperature Transmitter/Switch
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0005 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001-D04
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001-D04
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001-D02
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002-D00
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002-D01
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001-D04
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002-D06
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003-D06
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004-D06
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005-D06
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006-D06
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007-D06
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008-D06
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009-D06
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010-D06
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011-D06
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012-D06
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013-D06
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014-D06
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015-D06
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016-D06
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017-D06
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018-D06
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019-D06
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020-D06
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021-D05
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022-D06
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023-D06
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024-D06
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025-D06
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001-D04
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002-D02
D02

## NOTES
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For Temperature Transmitter/Switch
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 7
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0005 | D02
GENERAL NOTES:
1- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as the minimum and shall be verified by vendor.
2 - Vendor is responsible for the selection of Materials suitable for the specified working conditions.
3 - All lines below 4", shall be expanded to 4" to be suitable for thermowell installation.
4- Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
• Tag Number • Range Limit • Service • Manufacture Model
5- All transmitters shall have output short circuit & reverse polarity protection.
6- Sunshade to be considered for all transmitters.
7- All transmitters shall have a none-volatile EEprom memory to be used for storing the configuration data and sensor linearization data. This data must be retained in the transmitter to be functional upon power up.
8- Vendor shall identify and detail any deviation from the present instrument datasheet.
9- All transmitters shall be equipped with internal diagnostics software.
10- Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB for Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0

## TT
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For Temperature Transmitter/Switch
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 7
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN | DT | 0005 | D02
TEMPERATURE TRANSMITTER
GENERAL DATA |  |  | 1 | Tag No. | [7 empty] | SEE PAGE 6 & 7
|  |  | 2 | P&ID |  |  |  | Service |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 3 | Piping Class |  |  |  | Line No. |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 4 | Line Size |  |  |  | Schedule |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 5 | Area Clacification | [7 empty] | Zone 2- IIB T4
|  |  |  | RFI Protection |  |  |  | Tropicalisation |  |  |  | NEEDED |  | NEEDED
PROCESS CONDITION |  |  | 6 | Fluid |  |  |  | Phase |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 7 | Operating Temperature |  |  |  | Design Temperature |  |  | (°C) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 8 | Operating Pressure |  |  |  | Design Pressure |  |  | (barg) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 9 | Density (Winter) |  |  |  | Density (Summer) |  |  | (Kg/m3) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 10 | Viscosity (Winter) |  |  |  | Viscosity (Summer) |  |  | (C.P) | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 11 | Velocity | [6 empty] | (m/s) | SEE PAGE 6 & 7
TRANSMITTER |  |  | 12 | Thermoelement Type | [7 empty] | RTD
|  |  | 13 | Housing Material | [7 empty] | Die-Cast Aluminum
|  |  | 14 | Power Supply | [7 empty] | 24 VDC, Loop Powered
|  |  | 15 | Output Signal |  |  |  | Communication Protocol |  |  |  | 4-20 mA |  | HART (SMART TYPE)
|  |  | 16 | Instrument Range |  |  |  | Calibrated Range |  |  |  | SEE PAGE 6 & 7 |  | VTA
|  |  | 17 | Integral Digital Indicator |  |  |  | Scale |  |  |  | Required |  | Calibrated in Engineering unit
|  |  | 18 | Accuracy | [7 empty] | +/- 0.1 % Calibrated Span
|  |  | 19 | Burn Out Direction | [7 empty] | Up Scale
|  |  | 20 | Ingress Protection |  |  |  | Electrical Certification |  |  |  | IP-65 as minimum |  | EEx ia, IIB T4
|  |  | 21 | Electrical Connection |  |  |  | Cable Gland |  |  |  | ISO M20 x 1.5 |  | Required
|  |  | 22 | Mounting | [7 empty] | Compact With Element
|  |  | 23 | Calibration Range |  |  |  | Write Protection |  |  |  | VTA |  | SEE PAGE 6 & 7 (Note 3)
HEAD |  |  | 24 | Head Type |  |  |  | Material |  |  |  | Top Mounted-Screwed |  | Die-cast aluminum with baked vinyl finish.
|  |  | 25 | Terminal Block | [7 empty] | With 4 Terminal Wires
|  |  | 26 | Weather Protection |  |  |  | Electrical Certification |  |  |  | IP-65 as minimum |  | EEx ia,IIB T4
|  |  | 27 | Electrical Connection |  |  |  | Cable Gland |  |  |  | ISO M20 |  | Required
|  |  | 28 | Nipple Size | [7 empty] | 1/2 " NPT
TEMPERATURE ELEMENT |  |  | 29 | Type | [7 empty] | RTD
|  |  | 30 | Resistance |  |  |  | Wire Size |  |  |  | 100 ohms at 0 degree Celsius. |  | VTA
|  |  | 31 | Single / Double |  |  |  | No. of Wires |  |  |  | SEE PAGE 6 & 7 |  | 3 Wires
|  |  | 32 | Sheath Material |  |  |  | Sheath OD |  |  |  | 316 S.S |  | VTA
|  |  | 33 | Stem Length |  |  |  | Leads |  |  |  | To Match Thermowell |  | VTA
|  |  | 34 | Mounting Thread |  |  |  | Sealing |  |  |  | 1/2 " NPT |  | Hermetical
|  |  | 35 | Accuracy | [7 empty] | Class A as per IEC 60751
THERMOWELL |  |  | 36 | Construction Type | [7 empty] | Drilled Bar Stock in Tapered Configuration
|  |  | 37 | Element Connection | [7 empty] | 1/2" NPT
|  |  | 38 | Size (in) |  |  |  | Rating (lbs) |  |  |  | SEE PAGE 6 & 7 |  | SEE PAGE 6 & 7
|  |  | 39 | Process Connection |  |  |  | Flange Facing / Finish (μm) |  |  |  | Flanged |  | SEE PAGE 6 & 7
|  |  | 40 | Insertion Length (U) mm |  |  |  | LAG Extension (T) mm |  |  |  | SEE PAGE 6 & 7 |  | VTA
|  |  | 41 | Flange Material |  |  |  | Well Material |  |  |  | 316L S.S |  | 316L S.S
|  |  | 42 | Wake Frequency Standard | [7 empty] | Required as per ASME PTC 19.3
|  |  | 43 | NACE Requirements | [7 empty] | SEE PAGE 6 & 7 (Note 1)
44
PURCHASING DATA |  |  | 45 | Model |  |  |  | Manufacturer |  |  |  | will be finalized later |  | will be finalized later
|  |  | 46 | Supplier |  |  |  | Order |  |  |  | will be finalized later |  | will be finalized later
47
NOTES :
VTA : Vendor to Advise VTC : Vendor to Confirm N/A: Not Applicable
(1) Thermowell wake frequency analysis (stress calculation) according to ASME Power Test
Code 19.3 shall be done & submitted by vendor.
(2) The element length shall be compatible with well length.
(3) The transmitters which shall be write protected are identified by note 2 in sheet 6. (Also see note 2 in sheet 7)

## TT LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Data Sheets For Temperature Transmitter/Switch
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO |  | 120 | IN | DT |  | 0005 |  | D02
TEMPERATURE TRANSMITTER LIST
Rev. | Item No. | Tag No. | P&ID No. | Service | Piping Class | Line/Equipment No. | Line Size | Fluid | Phase | Operating Temperature (°C) | Design Temperature (°C) | Operating Pressure (barg) | Design Pressure (barg) | Density (Kg/m3) | Viscosity (CP) | Velocity (m/s) | Instrument Range (°C) | Calibration Range (°C) | Projection Length (mm) | Size (in) | Rating /Facing | Max Insertion Length (U) mm | Nace
D02 | 1 | TIT-2102 | BK-GCS-PEDCO-120-PR-PI-0002-D04 | TO INLET K.O. DRUM | AN07 | GAS-111-0101-AN07-6"-PT | 6" | PROCESS GAS | GAS | 26.67~46.11 | 85 | 5.5 | 18.2 | 6.6642 | 0.011 | 16.15 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D02 | 2 | TIT-2104 | BK-GCS-PEDCO-120-PR-PI-0003-D04 | TO SLUG CATCHER | FN05 | GAS-111-0001-FN05-8"-PT | 8" | PROCESS GAS | GAS | 15~32 | 85 | 5.5 | 41.2 | 6.2141 | 0.011 | 17.17 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 600/RF | 300 | YES
D02 | 3 | TIT-2112 | BK-GCS-PEDCO-120-PR-PI-0005-D04 | INLET K.O. DRUM INPUT | AN07 | GAS-111-0005-AN07-10"-PT | 10" | PROCESS GAS | GAS | 37.17~19.23 | 85 | 5.3 | 9 | 6.1649 | 0.011 | 17.37 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D02 | 4 | TIT-2121A | BK-GCS-PEDCO-120-PR-PI-0007-D04 (1 of 3) | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101A) | AN05 | GAS-111-0031A-AN05-8"-ET | 8" | PROCESS GAS | GAS | 18.88~36.78 | 155 | 4.9 | 22 | 5.7715 | 0.011 | 14.21 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D02 | 5 | TIT-2124A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0007-D04 (1 of 3) | TO 1ST STAGE AIR COOLER (AE-2101A) | CN05 | GAS-111-0036A-CN05-6"-NP | 6" | PROCESS GAS | GAS | 113.1~124.8 | 155 | 19 | 22 | 15.3834 | 0.011 | 9.23 | VTA | 0-250 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D02 | 6 | TIT-2121B | BK-GCS-PEDCO-120-PR-PI-0007-D04 (2 of 3) | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101B) | AN05 | GAS-111-0031B-AN05-8"-ET | 8" | PROCESS GAS | GAS | 18.88~36.78 | 155 | 4.9 | 22 | 5.7715 | 0.011 | 14.21 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D02 | 7 | TIT-2124B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0007-D04 (2 of 3) | TO 1ST STAGE AIR COOLER (AE-2101B) | CN05 | GAS-111-0036B-CN05-6"-NP | 6" | PROCESS GAS | GAS | 113.1~124.8 | 155 | 19 | 22 | 15.3834 | 0.011 | 9.23 | VTA | 0-250 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D02 | 8 | TIT-2121C | BK-GCS-PEDCO-120-PR-PI-0007-D04 (3 of 3) | FROM 1ST STAGE GAS COMP. SUCTION DRUM (V-2101C) | AN05 | GAS-111-0031C-AN05-8"-ET | 8" | PROCESS GAS | GAS | 18.88~36.78 | 155 | 4.9 | 22 | 5.7715 | 0.011 | 14.21 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 300 | YES
D02 | 9 | TIT-2124C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0007-D04 (3 of 3) | TO 1ST STAGE AIR COOLER (AE-2101C) | CN05 | GAS-111-0036C-CN05-6"-NP | 6" | PROCESS GAS | GAS | 113.1~124.8 | 155 | 19 | 22 | 15.3834 | 0.011 | 9.23 | VTA | 0-250 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D02 | 10 | TIT-2126A | BK-GCS-PEDCO-120-PR-PI-0008-D04 (1 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-A) | CS00 | GAS-111-0037A-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 150 | 18.3 | 22 | 18.2771 | 0.011 | 7.77 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D02 | 11 | TIT-2125A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0008-D04 (1 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-A) | CS00 | GAS-111-0037A-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 150 | 18.3 | 22 | 18.2771 | 0.011 | 7.77 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D02 | 12 | TIT-2126B | BK-GCS-PEDCO-120-PR-PI-0008-D04 (2 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-B) | CS00 | GAS-111-0037B-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 150 | 18.3 | 22 | 18.2771 | 0.011 | 7.77 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D02 | 13 | TIT-2125B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0008-D04 (2 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-B) | CS00 | GAS-111-0037B-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 150 | 18.3 | 22 | 18.2771 | 0.011 | 7.77 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D02 | 14 | TIT-2126C | BK-GCS-PEDCO-120-PR-PI-0008-D04 (3 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-C) | CS00 | GAS-111-0037C-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 150 | 18.3 | 22 | 18.2771 | 0.011 | 7.77 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D02 | 15 | TIT-2125C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0008-D04 (3 of 3) | AFTER 1ST STAGE AIR COOLER (AE-2101-C) | CS00 | GAS-111-0037C-CS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 150 | 18.3 | 22 | 18.2771 | 0.01 | 7.77 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | NO
D02 | 16 | TIT-2131A | BK-GCS-PEDCO-120-PR-PI-0010-D04 (1 of 3) | FROM 2ND STAGE GAS COMP. SUCTION DRUM (V-2102A) | CN05 | GAS-111-0044A-CN05-6"-ET | 6" | PROCESS GAS | GAS | 59.88~59.89 | 175 | 18.1 | 62 | 18.0832 | 0.01 | 7.85 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D02 | 17 | TIT-2134A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0010-D04 (1 of 3) | TO 2ND STAGE AIR COOLER (AE-2102A) | FN05 | GAS-111-0051A-FN05-6"-IS | 6" | PROCESS GAS | GAS | 142.3/149.5 | 175 | 54.8 | 62 | 42.9225 | 0.01 | 3.31 | VTA | 0-300 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | YES
D02 | 18 | TIT-2131B | BK-GCS-PEDCO-120-PR-PI-0010-D04 (2 of 3) | FROM 2ND STAGE GAS COMP. SUCTION DRUM (V-2102B) | CN05 | GAS-111-0044B-CN05-6"-ET | 6" | PROCESS GAS | GAS | 59.88~59.89 | 175 | 18.1 | 62 | 18.0832 | 0.01 | 7.85 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D02 | 19 | TIT-2134B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0010-D04 (2 of 3) | TO 2ND STAGE AIR COOLER (AE-2102B) | FN05 | GAS-111-0051B-FN05-6"-IS | 6" | PROCESS GAS | GAS | 142.3/149.5 | 175 | 54.8 | 62 | 42.9225 | 0.01 | 3.31 | VTA | 0-300 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | YES
D02 | 20 | TIT-2131C | BK-GCS-PEDCO-120-PR-PI-0010-D04 (3 of 3) | FROM 2ND STAGE GAS COMP. SUCTION DRUM (V-2102C) | CN05 | GAS-111-0044C-CN05-6"-ET | 6" | PROCESS GAS | GAS | 59.88~59.89 | 175 | 18.1 | 62 | 18.0832 | 0.01 | 7.85 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 300/RF | 250 | YES
D02 | 21 | TIT-2134C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0010-D04 (3 of 3) | TO 2ND STAGE AIR COOLER (AE-2102C) | FN05 | GAS-111-0051C-FN05-6"-IS | 6" | PROCESS GAS | GAS | 142.3/149.5 | 175 | 54.8 | 62 | 42.9225 | 0.01 | 3.31 | VTA | 0-300 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | YES
D02 | 22 | TIT-2135A | BK-GCS-PEDCO-120-PR-PI-0011-D04 (1 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-A) | FS00 | GAS-111-0058A-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 175 | 54.1 | 62 | 59.6327 | 0.01 | 2.38 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D02 | 23 | TIT-2136A (Note 2) | BK-GCS-PEDCO-120-PR-PI-0011-D04 (1 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-A) | FS00 | GAS-111-0058A-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 175 | 54.1 | 62 | 59.6327 | 0.01 | 2.38 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D02 | 24 | TIT-2135B | BK-GCS-PEDCO-120-PR-PI-0011-D04 (2 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-B) | FS00 | GAS-111-0058B-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 175 | 54.1 | 62 | 59.6327 | 0.01 | 2.38 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D02 | 25 | TIT-2136B (Note 2) | BK-GCS-PEDCO-120-PR-PI-0011-D04 (2 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-B) | FS00 | GAS-111-0058B-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 175 | 54.1 | 62 | 59.6327 | 0.01 | 2.38 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D02 | 26 | TIT-2135C | BK-GCS-PEDCO-120-PR-PI-0011-D04 (3 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-C) | FS00 | GAS-111-0058C-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 175 | 54.1 | 62 | 59.6327 | 0.01 | 2.38 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D02 | 27 | TIT-2136C (Note 2) | BK-GCS-PEDCO-120-PR-PI-0011-D04 (3 of 3) | AFTER 2ND STAGE AIR COOLER (AE-2102-C) | FS00 | GAS-111-0058C-FS00-6"-NP | 6" | PROCESS GAS | GAS | 60 | 175 | 54.1 | 62 | 59.6327 | 0.01 | 2.38 | VTA | 0-120 | 162 NOTE 1 | 1 1/2" | 600/RF | 250 | NO
D02 | 28 | TT-2211 | BK-GCS-PEDCO-120-PR-PI-0016-D04 | NITROGEN RECEIVER OUTLET | AN01 | NIT-112-0024-AN01-2"-PT | 2" | NITROGEN | GAS | 60 | 85 | 8 | 12.5 | 8.62 | 0.019 | 0.63 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 200 (NOTE 3 IN GENERAL NOTES) | NO
D02 | 29 | TIT-2271 | BK-GCS-PEDCO-120-PR-PI-0022-D04 | FUEL GAS K.O. DRUM OUTLET | AN07 | FLG-112-0110-AN07-2"-PT | 2" | FUEL GAS | GAS | 32 | 85 | 0.5 | 9 | 5.7715 | 0.01 | 0.64 | VTA | 0-100 | 162 NOTE 1 | 1 1/2" | 300/RF | 200 (NOTE 3 IN GENERAL NOTES) | YES
NOTES:
(1) Projection Length (mm) will be finallized by piping department.
(2) Transmitters shall be of the smart transmitter type with HART communication protocol, except those connected to the ESD/HIPPS/FGS system that will be preferably of conventional electronic type. If smart type transmitters are selected for ESD application they shall be configured as “write protection”.
D02
D02
D02
D02
D02
D02
D02
D02