## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0005_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1636 |  |  | Transmital Date: 28 Nov 2022
Document Title: Data Sheets For Temperature Transmitter/Switch |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1636 |  |  | Transmital Date: 28 Nov 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-DT-0005_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ذكر گردد كه مطالعات wake frequencies بايد توسط وندور انجام شود. |  | BK-SUR-ENG-INS-01-06417 | 2022-12-17 | در صفحه 5 مدرک تحت عنوان Note 1 ذکر شده است
2 | Calibration Range براي ادوات بر اساس دماي طراحي اصلاح شود. |  | BK-SUR-ENG-INS-01-06417 | 2022-12-17 | اصلاح گردید
3 | Write Protection در صفحه 6 و 7 اصلاح شود. |  | BK-SUR-ENG-INS-01-06417 | 2022-12-17 | اصلاح شد
4 | آيتم 31 در صفحه 6 و 7 اصلاح شود. |  | BK-SUR-ENG-INS-01-06417 | 2022-12-17 | اصلاح شد
5 | رنج کالیبراسیون با توجه به دمای طراحی اصلاح گردد. ( به عنوان نمونه TIT-2112 و TIT-2121) |  | BK-SUR-ENG-INS-01-06417 | 2022-12-17 | اصلاح گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 17 Dec 2022 |  |  |  |  | Date: