## WALL THICKNESS
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
WALL THICKNESS CALCULATION REPORT
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 | [6 empty] | BK |  | PPL | PEDCO |  | 320 | PI | RT |  | 0002 |  | D03
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN01 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.150 - PN 20, R.F. |  |  | 1 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 18.2 | D03
SERVICE |  | Oily Water
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 1 | 1.152 | 0.875 | 1.317 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 1 | 1.178 | 0.875 | 1.346 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 1 | 1.229 | 0.875 | 1.405 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 1 | 1.305 | 0.875 | 1.491 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 1 | 1.406 | 0.875 | 1.607 | 3.91 | Sch 40 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 1 | 1.584 | 0.875 | 1.81 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 1 | 1.762 | 0.875 | 2.014 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 1 | 2.092 | 0.875 | 2.391 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 1 | 2.448 | 0.875 | 2.798 | 6.35 | Sch 20 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 1 | 2.803 | 0.875 | 3.203 | 6.35 | Sch 20 | 10
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN07 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.150, R.F. |  |  | 6 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 18.2 | D03
SERVICE |  | Hydrocarbon Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 6 | 6.152 | 0.875 | 7.031 | 7.47 | Sch XXS | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 6 | 6.178 | 0.875 | 7.061 | 7.82 | Sch XXS | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 6 | 6.229 | 0.875 | 7.119 | 9.09 | Sch XXS | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 6 | 6.305 | 0.875 | 7.206 | 10.15 | Sch XXS | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 6 | 6.406 | 0.875 | 7.321 | 8.74 | Sch 160 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 6 | 6.584 | 0.875 | 7.525 | 7.62 | Sch 80 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 6 | 6.762 | 0.875 | 7.728 | 8.56 | Sch 80 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 6 | 7.092 | 0.875 | 8.105 | 10.97 | Sch 80 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 6 | 7.448 | 0.875 | 8.512 | 10.31 | Sch 60 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 6 | 7.803 | 0.875 | 8.918 | 9.27 | Sch 40 | 10
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
CN05 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.300, R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 46.9 | D03
SERVICE |  | Condensate Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.014 | 0.356 | 0.14 | 3.55 | 3 | 3.356 | 0.875 | 3.835 | 3.84 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.018 | 0.457 | 0.175 | 4.45 | 3 | 3.457 | 0.875 | 3.951 | 3.94 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.022 | 0.559 | 0.219 | 5.567 | 3 | 3.559 | 0.875 | 4.067 | 4.07 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.032 | 0.813 | 0.317 | 8.05 | 3 | 3.813 | 0.875 | 4.358 | 4.35 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.04 | 1.016 | 0.396 | 10.05 | 3 | 4.016 | 0.875 | 4.59 | 4.59 | Sch 80 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.059 | 1.499 | 0.583 | 14.817 | 3 | 4.499 | 0.875 | 5.142 | 5.14 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.076 | 1.93 | 0.75 | 19.05 | 3 | 4.93 | 0.875 | 5.634 | 5.62 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 46.9 | 680.3 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.111 | 2.819 | 1.104 | 28.05 | 3 | 5.819 | 0.875 | 6.65 | 6.66 | Sch 40 | 6
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
FN05 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.600, R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 94 | D03
SERVICE |  | Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.028 | 0.711 | 0.14 | 3.55 | 3 | 3.711 | 0.875 | 4.241 | 4.78 | Sch.160 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.035 | 0.889 | 0.175 | 4.45 | 3 | 3.889 | 0.875 | 4.445 | 5.56 | Sch.160 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.044 | 1.118 | 0.219 | 5.567 | 3 | 4.118 | 0.875 | 4.706 | 6.35 | Sch.160 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.063 | 1.6 | 0.317 | 8.05 | 3 | 4.6 | 0.875 | 5.257 | 7.14 | Sch.160 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.079 | 2.007 | 0.396 | 10.05 | 3 | 5.007 | 0.875 | 5.722 | 8.74 | Sch.160 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.116 | 2.946 | 0.583 | 14.817 | 3 | 5.946 | 0.875 | 6.795 | 7.62 | Sch.80 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.149 | 3.785 | 0.75 | 19.05 | 3 | 6.785 | 0.875 | 7.754 | 8.08 | Sch.80 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.22 | 5.588 | 1.104 | 28.05 | 3 | 8.588 | 0.875 | 9.815 | 10.97 | Sch.80 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.286 | 7.264 | 1.438 | 36.517 | 3 | 10.264 | 0.875 | 11.73 | 12.7 | Sch.80 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.357 | 9.068 | 1.792 | 45.5 | 3 | 12.068 | 0.875 | 13.792 | 15.59 | Sch.80 | 10
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
FN07 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.600, R.F. |  |  | 6 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 94 | D03
SERVICE |  | Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.028 | 0.711 | 0.14 | 3.55 | 6 | 6.711 | 0.875 | 7.67 | - | - | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.035 | 0.889 | 0.175 | 4.45 | 6 | 6.889 | 0.875 | 7.873 | - | - | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.044 | 1.118 | 0.219 | 5.567 | 6 | 7.118 | 0.875 | 8.135 | 9.09 | Sch XXS | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.063 | 1.6 | 0.317 | 8.05 | 6 | 7.6 | 0.875 | 8.686 | 10.15 | Sch XXS | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.079 | 2.007 | 0.396 | 10.05 | 6 | 8.007 | 0.875 | 9.151 | 11.07 | Sch XXS | 2
3 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.116 | 2.946 | 0.583 | 14.817 | 6 | 8.946 | 0.875 | 10.224 | 11.13 | Sch 160 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.149 | 3.785 | 0.75 | 19.05 | 6 | 9.785 | 0.875 | 11.183 | 13.49 | Sch 120 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.22 | 5.588 | 1.104 | 28.05 | 6 | 11.588 | 0.875 | 13.243 | 14.27 | Sch 120 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.286 | 7.264 | 1.438 | 36.517 | 6 | 13.264 | 0.875 | 15.159 | 18.26 | Sch 120 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 94 | 1363.4 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.357 | 9.068 | 1.792 | 45.5 | 6 | 15.068 | 0.875 | 17.221 | 18.26 | Sch 100 | 10