## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DC-0001_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-NISOC-T-1348 |  |  | Transmital Date: 3 Sep 2023
Document Title: Fire & Gas Detection Design Criteria |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1348 |  |  | Transmital Date: 3 Sep 2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DC-0001_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در بخش 8 صفحه 17، در خصوص نوع طبقه بندی منطقه خطر تجهیزات به نقشه های Hazardous Area Classification Layout ارجاع داده شود. |  | 01/2294/283311 | 1401/08/05 | در دو بند آخر در بخش 8 به این مدرک اشاره شده است.
All materials and equipment’s associated with Fire & Gas detection/control shall be suitable for being used within Zone 2 hazardous area and the prevailing environmental conditions (Refer to Specification for Hazardous Area Classification Doc. No.: BK-GNRAL-PEDCO-000-SA-SP-0002) Field devices shall be certified for electrically hazardous environment Zone 2, Class IIB, T4 as minimum and ingress protection IP65 (Refer to Specification for Hazardous Area Classification Doc. No.: BK-GNRAL-PEDCO-000-SA-SP-0002).
2 | در بخش 8.3.1 صفحه در زمان فعال شدن یک دتکتور درون ساختمان لازم است آلارم دیداری و شنیداری ساختمان فعال گردد. |  | 01/2294/283311 | 1401/08/05 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
3 | در بخش های 9.2،9.4،9.5،9.6 منطق 200N مربوط به دتکتور در سطح بالا (50LEL% و 20 PPM) لحاظ شود و آلارم شنیداری پیوسته و دیداری فعال شوند. |  | 01/2294/283311 | 1401/08/05 | این مورد در مدرک وجود داردتنها عبارت (voting 2ooN) به توضیحات مربوطه اضافه گردید.
4 | در 9.7 صفحه 24، منطق 2OON مربوط به دتکتور در سطح بالا (10% LEL) لحاظ شود و آلارم شنیداری پیوسته و دیداری فعال شوند. |  | 01/2294/283311 | 1401/08/05 | این مورد در مدرک وجود داردتنها عبارت (voting 2ooN) به توضیحات مربوطه اضافه گردید.
5 | در 9.7 صفحه 24، با فعال شدن یک دتکتور درحالت 10% LEL، Isolation of battery feeder and Shutdown of battery boost chargingنیز فعال گردد. |  | 01/2294/283311 | 1401/08/05 | مدرک مطابق خواست کارفرمای محترم اصلاح گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 18 Sep 2022 |  |  |  |  | Date: