## Cover
| NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
| 9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | DT | 0009 | D03
Mechanical Data Sheets For Nitrogen Receiver (V-2204) / sheet 4 of 4 | طرح نگهداشت و افزایش تولید 27 مخزن
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER نگهداشت و افزایش تولید میدان نفتی بینک
| D03 |  | JUN.2023 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | A.M.Mohseni
| D02 |  | SEP.2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
| D01 |  | DEC. 2021 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
| D00 |  | NOV.2021 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
| Class: 1 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-708840
| status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | DT | 0009 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X |  | X | [5 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Notes (1)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0009 | D03
General Notes
Rev
| 1. | The Asterisk * denotes information and/or confirmation required from VENDOR.
| 2. | Deleted
| 3. | VENDOR shall include for the services of a independent verification body for mechanical design, stage inspection, testing and
stamping of the equipment (if possible).
| 4. | Painting and coating (internal & external) shall be as per project 'Specification for Painting', Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006.
and Specification For Lining Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0007 respectively.
| 5. | Flanges shall comply with ASME B16.5. Nozzle bolt holes shall straddle the natural centrelines for horizontal nozzles.
VENDOR to confirm maximum allowable nozzle loads and moments (RF: Raised Face, WN: Welding Neck)
| 6. | All reinforcement pads shall have 1/4" (6mm) tell-tale hole and 1/8" (3mm) vent hole as per Standard Detail Drawing For Pressure Vessels
and Heat Exchangers', Doc. No. BK-GNRAL-PEDCO-000-ME-DW-0001".
| 7. | Manways shall be supplied complete with blind flange, external grab handles, internal grab handle and ladder rungs, nuts, bolting, gasket and
proof load test davits. Davits shall be proof load tested on the vessels to 1.5 x Safe Working Load (SWL) and shall be marked accordingly.
| 8. | All external bolts and nuts shall be hot dip galvanized. Internal bolts and nuts shall be stainless steel.
| 9. | Loads at support base, Shall be calculated and determined by vendor.
| 10. | Access Ladder & Platform to be considered .
| 11. | Deleted
| 12. | All material, corrosion allowance and their suitability for the process fluid at design pressure and temperature to be confirmed by vendor.
| 13. | Deleted
| 14. | All nozzle locations and orientations will be finalized later.
| 15. | Instrumentation items are excluded from vendor's scope of supply.
| 16. | Any changes in material of construction, location & orientation of the nozzles shall be confirmed by client.
| 17. | All materials shall be new and unused.
| 18. | Fabrication tolerances for vessel shall be in accordance with requirement of ASME code.
| 19. | Location and number of lifting lugs on vessels shall be specificed on VENDOR drawing.
| 20. | All items shall be clearly match marked against vessel drawings to facilitate erection.
| 21. | Deleted
| 22. | Vendor shall supply details of all welding connections and give general specification of used materials.
| 23. | For equipment requiring PWHT, final inspection and acceptance by the CLIENT or its nominated representative shall only be
undertaken against NDE after PWHT. All weldings shall be made before vessel heat treatment (if any).
| 24. | Equipment packaging, preparation for shipment and delivery shall be in accordance with the project Minimum Requirements for Marking,
Packing, Shipment & Storage' Document No. IPS-G-GN-210.
| 25. | Specified accessories and attachments shall be supplied by vendor.
| 26. | Gasket shall be spiral wound type, graphite filled with inner ring and outer ring S.S.316
| 27. | Deleted
| 28. | Deleted
| 29. | Two M12 earthing lugs shall be provided on vessel support. Material of Earthing lugs shall be S.S. 316

## Notes (2)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0009 | D03
General Notes (Cont'd)
Rev
| 30. | For standard detail of Earth lug execution refer to the Project "Standard Detail Drawing For Pressure Vessels and Heat Exchangers
Doc. No. BK-GNRAL-PEDCO-000-ME-DW-0001".
| 31. | Elliptical heads shall be Ultrasonic Tested for lamination after forming.
| 32. | The projection of equipment's nozzles should be considered as per 'Standard Detail Drawing For Pressure Vessels and Heat Exchangers',
Doc. No. BK-GNRAL-PEDCO-000-ME-DW-0001". Projection of Horizontal & Vertical nozzles is from tengent line and centerline respectively.
| 33. | The elevation of equipment's nozzels should be specified as follows :
I. For vertical vessels : from bottom T.L.
II. For horizontal vessels : from Left T.L.
| 34. | Nozzles and flanges shall be suitably supported and reinforced based on nozzle loads provided in project Specification for Pressure Vessels,
Document No. BK-GNRAL-PEDCO-000-ME-SP-0001.
| 35. | Prior to sealing the vessel for shipping and storage, the inside surface of the equipment shall be 100% visually inspected. Internal
surfaces shall be clean and thoroughly dried. The CLIENT or its nominated representative shall witness the cleanliness of internal
surfaces. Flange faces shall be protected by wooden or plastic dummy flanges.
| 36. | Minimum requirement for pre-commissioning, commissioning, start up and two years operation and spare parts shall be in accordance with
document E&C-QC-SP-1.
| 37 | Lifting Lugs / trunnions shall be provided to facilitate a single point lift. If a single point lift cannot be achieved without the use of a lifting
beam, then VENDOR shall provide a suitable, certified, lifting beam.
| 38. | Design pressure specified is at top of vessels. VENDOR design shell include static head for vessels flooded with specific gravity of
the handled liquid.
| 39. | VENDOR is to maximize shop fabrication based on the following transportation limits:
- Maximum weight: 96 tonnes
- Maximum load per axle: 12 tonnes
- Maximum length: 50.0 m
- Maximum width: 5.0 m
- Maximum height: 5.2 m
For items with dimensions and weights greater than the road capacity specified above, VENDOR may be required to split the package
into several components.
| 40. | All external attachments directly welded to the pressure part shall be the same material as vessel grade.
| 41. | The Vendor shall be fully responsible for the complete mechanical design, preparing calculation book and supply of the vessel.
| 42. | All dimensions shown are in mm unless otherwise indicated. All nozzle sizes are in inch.

## V-2204 (1)
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
شماره پیمان: | [6 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 5 از 8
9184 – 073 - 053 | [6 empty] | BK | GCS |  | PEDCO | 120 | ME |  | DT | 0009 |  |  | D03
Mechanical Data Sheets For Nitrogen Receiver (V-2204) / sheet 1 of 4
Rev | DATA SHEET | [20 empty] | Rev
| 1 | Description | : |  | Nitrogen Receiver
| 2 | Tag No. | : |  | V-2204 | [7 empty] | Quantity |  |  | : | 1 |  | Set
| 3 | Type | : |  | Pressure Vessel
| 4 | Process Design Data
| 5 | Contents | [10 empty] | Corrosive / Erosive
| 6 | Operating Temp. |  |  | (oC) | 60 | [6 empty] | Liquid Flow |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | 8 | [6 empty] | Vap. Molec. Weight |  |  |  | (kg/kmol)
| 8 | Gas Flow | (kg/h) |  |  | 32.5 | [6 empty] | Liquid Sp. Gravity | [7 empty] | 1
| 9 | Liquid Viscosity |  | (cP) | [8 empty] | Service: | [7 empty] | N/A
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [6 empty] | Vessel Orientation | [7 empty] | Vertical
| 12 | Design Press. | (barg) |  |  | 12.5 | [6 empty] | Liquid Level |  |  |  | (mm) |  |  |  | 300
| 13 | Test Press. | (barg) |  |  | Per Code & Specification | [6 empty] | Nor. Liquid Vol. |  |  |  | (m3)
| 14 | Internal Vacuum |  | (barg) |  | - | [6 empty] | In. Dia. Of Boots |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 1050 | [6 empty] | Boot Length |  |  |  | (mm) |  |  |  | N/A
| 16 | Tan/Tan Dim. | (mm) |  |  | 3150 | [6 empty] | Boot Head Type | [7 empty] | N/A
| 17 | Vessel Head Type |  |  |  | 2:1 elliptical | [6 empty] | Corr. Allowance |  |  |  | (mm) |  |  |  | 1.6
| 18 | Shell Wall Thk. | (mm) |  |  | * | [6 empty] | Joint Efficiency | [7 empty] | 0.7 (Skirt)/ 0.85 (Shell) /1(Head)
| 19 | Head Wall Thk. | (mm) |  |  | * (After Forming) | [6 empty] | Ambient Temp. |  |  |  | (oC)
| 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [6 empty] | MDMT |  |  |  | (oC) |  |  |  | 5
| 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [6 empty] | Insulation Required | [7 empty] | No
| 22 | Materials
| 23 | Code |  |  |  |  | ASME II / ASTM | [5 empty] | Nozzle Necks:
| 24 | Shell |  |  |  |  | A 516 Gr. 70 | [5 empty] | Pipes | [7 empty] | A 106 Gr.B
| 25 | Heads |  |  |  |  | A 516 Gr. 70 | [5 empty] | Plates | [7 empty] | A 516 Gr.70
| 26 | Lining / Cladding |  |  |  |  | P3 | [5 empty] | Forgings | [7 empty] | A 105
| 27 | Skirt (Top / Bottom) |  |  |  |  | A 516 Gr. 70 / A 283 Gr. C | [5 empty] | Flanges | [7 empty] | A 105
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. | [5 empty] | Fittings | [7 empty] | A 234 Gr. WPB
| 29 | Gaskets |  |  |  |  | Note 26 | [5 empty] | External Bolts | [7 empty] | A 193 Gr. B7 (Note 8)
| 30 | Lifting Lugs |  |  |  |  | A 516 Gr.70 / A 283 Gr. C | [5 empty] | External Nuts | [7 empty] | A 194 Gr. 2H (Note 8)
| 31 | Reinforcing Pads |  |  |  |  | A 516 Gr.70 | [5 empty] | Internal Bolts / Nuts | [7 empty] | S.S.
| 32 | Ladder & Platform |  |  |  |  | C.S. | [5 empty] | Name Plate | [7 empty] | S.S. 316
33
| 34 | REFERENCE STANDARDS & DOCUMENTS
| 35 | Mechanical Design Code | [10 empty] | ASME Sec VIII Div 1, IPS-G-ME-150
| 36 | Specification for Pressure Vessels | [10 empty] | BK-GNRAL-PEDCO-000-ME-SP-0001
| 37 | Process Basis of Design | [10 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 38 | Piping & Instrument Diagram (P&ID) | [10 empty] | BK-GCS-PEDCO-120-PR-PI-0016
| 39 | Specification for Painting | [10 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 40 | Specification for Insulation | [10 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
41
42
| 43 | Fabrication and Inspection Requirements
| 44 | Inspection Authority |  |  |  |  | TPI & Client
| 45 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1, Minimum for Pressure Containing and Attachments
| 46 | Hydro Test Medium |  |  |  |  | Water | [5 empty] | Hydro Test Procedure | [6 empty] | Yes;Per Code & Spec. Requirements
| 47 | Post Weld Heat Treatment |  |  |  |  | Per Code & Spec Requirements | [5 empty] | PT | [6 empty] | 100%
| 48 | MT |  |  |  |  | 100 % on Lifting Lug Fillet Welds | [5 empty] | UT | [6 empty] | Yes;Per Code & Spec. Requirements
| 49 | RT |  |  |  |  | 100 | % | On T-Joints and Head Joints Butt-Welds,
| 50 | [5 empty] | Spot |  | On Shell Longitudinal and Circumferential Joints Butt-Welds,
| 51 | [5 empty] | 100 | % | On Nozzle Neck to Flange & Fabricated Nozzle Neck Longitudinal Butt-Welds,
| 52 | RT Report |  |  |  |  | Yes; Per Code & Spec. Requir. | [5 empty] | PT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 53 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. | [5 empty] | UT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 54 | Fabrication Quality Control Plan (With Offer) | [10 empty] | Yes
| 55 | Welding Procedure Review / Approval | [10 empty] | Yes
| 56 | Surface Preparation & Coating | [10 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006" Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
57
58
59
60
61
62
63

## V-2204 (2)
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 6 از 8
9184 – 073 - 053 | [6 empty] | BK |  | GCS | PEDCO | 120 | ME |  | DT | 0009 |  | D03
Mechanical Data Sheets For Nitrogen Receiver (V-2204) / sheet 2 of 4
Rev. | ACCESSORIES , NOZZLES LIST & LOADS @ BASE | [22 empty] | Rev.
| 1 | Accessories & Attachments (Note 25)
| 2 | Supporting Saddles | [8 empty] | NO |  | Name Plate Bracket | [9 empty] | YES
| 3 | Access Ladder & Platform | [8 empty] | YES |  | Name Plate | [9 empty] | YES
| 4 | Insulation Support | [8 empty] | NO |  | Earthing Lug (Note 30) | [9 empty] | YES
| 5 | Insulation | [8 empty] | NO |  | Tailing Lug | [9 empty] | YES
| 6 | Insulation Cover | [8 empty] | NO |  | Cathodic Protection (Sacrificial Anodes) | [9 empty] | NO
| 7 | Fireproofing Support | [8 empty] | NO |  | Anchor Bolts | [9 empty] | NO
| 8 | Lifting Lugs | [8 empty] | YES |  | Instrumentations | [9 empty] | NO
| 9 | Internal/ External Clips | [8 empty] | YES |  | Skid | [9 empty] | NO
| 10 | Template | [8 empty] | YES |  | Support Clips | [9 empty] | YES
| 11 | Boot | [8 empty] | NO |  | Vortex Breaker | [9 empty] | YES
| 12 | Davit for Manhole | [8 empty] | YES |  | Rung & Grip | [9 empty] | NO
| 13 | Internal Lining (By Painting) | [8 empty] | YES |  | Heating Coil | [9 empty] | NO
14
15
16
17
| 18 | Nozzles List (Note 1, 3, 5, 9, 12, 41)
| 19 | Mark |  | Qty. |  | Description |  |  |  | Pipe |  |  |  | Flange |  |  |  | Proj. | (mm) | Reinforcement |  | Remarks
| 20 | [8 empty] | Size | Thk. | Sch. |  | Type | Rate. | Face |  | (Note 32) |  | Thk. | O.D.
| 21 | A |  | 1 |  | Inlet |  |  |  | 2" |  |  |  | WN | #150 | RF |  | 741
| 22 | B |  | 1 |  | Gas Outlet |  |  |  | 2" |  |  |  | WN | #150 | RF |  | See DWG
| 23 | PSV |  | 1 |  | Pressure Safety Valve |  |  |  | 2" |  |  |  | WN | #150 | RF |  | 741
| 24 | V |  | 1 |  | Vent |  |  |  | 2" |  |  |  | WN | #150 | RF |  | See DWG
| 25 | M |  | 1 |  | Manhole |  |  |  | 24" |  |  |  | WN | #150 | RF |  | 791 |  | * | * | Note 7
| 26 | P |  | 1 |  | Pressure Gauge |  |  |  | 2" |  |  |  | WN | #300 | RF |  | 741
| 27 | D |  | 1 |  | Drain |  |  |  | 2" |  |  |  | WN | #150 | RF |  | See DWG
| 28 | L 1,2 |  | 2 |  | Level Gauge |  |  |  | 2" |  |  |  | WN | #300 | RF |  | 741
29
30
31
32
33
34
35
36
37
38
39
40
41
42
| 43 | Wind and Seismic Loads at Base * Note(9)
| 44 |  | Load Condition |  | Empty Condition | [5 empty] | Operating Condition | [5 empty] | Testing Condition
45
| 46 |  |  |  | Max. Shear @ Base (Kg) |  |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg) | Max. Shear @ Base (Kg) |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg) |  | Max. Shear @ Base (Kg) |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg)
47
| 48 |  | Load Type
49
50
| 51 | WIND
52
| 53 | SEISMIC
54
55
56
57
58
59
60
61
62
63
64
65

## V-2204 (3)
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 8
9184 – 073 - 053 | BK | GCS | PEDCO | 120 | ME | DT | 0009 | D03
Mechanical Data Sheets For Nitrogen Receiver (V-2204) / sheet 3 of 4
Sketch

## V-2204 (4)
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR NITROGEN RECEIVER
شماره پیمان: | [6 empty] | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 8 از 8
9184 – 073 - 053 | [6 empty] | BK | GCS |  | PEDCO |  | 120 | ME |  | DT | 0009 |  | D03
Mechanical Data Sheets For Nitrogen Receiver (V-2204) / sheet 4 of 4
Rev. | WEIGHT | [21 empty] | Rev.
| 1 | WEIGHT CONTROL DATA SHEET SI UNIT * | [12 empty] | 1/1
2
3
4
5
| 6 | Service |  | : |  | Nitrogen Receiver | [8 empty] | Location |  | : | Bushehr (Binak Oilfield)
| 7 | Type |  | : | [10 empty] | Quotation No. |  | :
| 8 | No. trains |  | : | [10 empty] | Serial No. |  | :
| 9 | No. stages |  | :
| 10 | Supplier |  | :
| 11 | Manufacturer |  | :
| 12 | Model |  | :
13
| 14 | Note: Information to be completed by equipment vendor.
15
| 16 | Total weight (kg) *
| 17 | Fabrication |  |  | Erection |  |  |  | Operation |  |  |  |  | Hydrostatic Test |  |  |  | Removable internal |  |  | Ladder & Platform
18
19
20
21
22
| 23 | WEIGHT AND C OF G DATA REQUIRED *
| 24 | CONDITION |  |  |  | WEIGHT ACCURACY % |  |  |  |  | WEIGHT (kg) |  |  |  |  | CENTER OF GRAVITY (mm)
| 25 | [14 empty] | X |  |  | Y |  |  | Z
| 26 | Dry
27
28
29
| 30 | SKETCH
31
32
33
| 34 | [13 empty] | ASME BPVC VIII, DIV.1
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
| 52 | NOTES
| 53 | 1) | All lifting points to be load tested and certified.
| 54 | 2) | Any spreader beam to be load tested and certified.
| 55 | 3) | Lifting / rigging plan for skid mounted equipment to be provided by the Vendor.
56
57
58
59
60
61
62
63