## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-CN-0006_D05 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2051 |  |  | Transmital Date: 4/30/2023
Document Title: Calculation Note For Control Valve Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-2051 |  |  | Transmital Date: 4/30/2023
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-CN-0006_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در مدرک مذکور فقط اطلاعات مربوط به FCV و PCV لحاظ شده است در صورتی که می بایست اطلاعات و محاسبات مربوط به LCV ها نیز درج گردد. |  | 1402-2294-127226 | 1402/04/04 | اعمال گردید.
2 | در خصوص FCV-2111 شماره نقشه اشتباه بیان شده است. |  | 1402-2294-127226 | 1402/04/04 | اصلاح گردید.
3 | سایز شیرهای کنترلی می بایست مطابق محاسبات سازنده نهایی شود. شروع محاسبات طراحی با پیش فرض یک سایز کوچکتر از خط لوله با محدودیت حداقل سایز مساوی با نصف خط لوله می باشد. در صورت کمتر بودن از یک سایز نهایی شدن طراحی پس از ارائه محاسبات و مطابق استاندارد خواهد بود. |  | 1402-2294-127226 | 1402/04/04 | مطابق بند فوق سایز شیرهای کنترلی اصلاح گردید.
4 | مطابق تصمیمات اخذ شده در جلسات بررسی مدارک مهندسی سطح الارض در تاریخ 1402/03/22 می بایست کلیه نظرات مربوط به شیرهای کنترلی و تصمیمات اخذ شده ملاک عمل قرار گیرد. |  | 1402-2294-127226 | 1402/04/04 | مورد تایید است
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: