## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-BD-0001_D05 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1725 |  |  | Transmital Date: 24 Dec 2022
Document Title: Control/ESD/F&G System Block Diagram Configuration |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1725 |  |  | Transmital Date: 24 Dec 2022
[5 empty] | CRS No:NISOC-CRS-BK-GCS-PEDCO-120-IN-BD-0001_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در خصوص مورد ۸ ، برای مجموعه نمزدا مانعی ندارد از سیستم کنترلی Type B استفاده شود ولی سیستم کنترلی گرمکن (BMS) لازم است بصورت مستقل با الزامات استانداردی درنظرگرفته شود. در استاندارد NFPA 87 که برای گرمکن های بزرگتر از 44kw میباشد،‌ برخی از الزامات استانداردی برای BMS وPLC آن مطرح شده است. |  | 1401/2294/389221 | 1401/10/13 | سیستم کنترل نمزدا در این مدرک مطابق آخرین توافقات به صورت type C با پانل مستقل ESD/BMS در نظر گرفته شد.
2 | در خصوص موارد دیگر در حال حاضر نظر خاصی مطرح نمیباشد و پس از نهایی سازی مدرک مهندسی سازندگان پکیج ها لازم است این مدرک نیز بروزرسانی شود. |  | 1401/2294/389221 | 1401/10/13 | مدرک مطابق آخرین توافقات به روز رسانی گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 8 Jan 2023 |  |  |  |  | Date: