## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-LD-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1178 |  |  | Transmital Date: 23 Jul 2022
Document Title: Control System Logic Diagram |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR- 1178 |  |  | Transmital Date: 23 Jul 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-LD-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | ملاحظه شد.
2 | شماتيك با استفاده از نتايج به دست آمده از جلسات HAZID/HAZOP/SIL مجددا بررسي و اصلاح گردد. (براي مثال قرار شد PAL-2102 در نظر گرفته شود.) |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
3 | بازگشت به كامنت شماره2، قرار بر اين شد كه Auto Start حذف گردد. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
4 | تگ پمپ در صفحه 21 اصلاح شود. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
5 | بازگشت به كامنت هاي پيشين و نظر كارفرما سه عدد UCP براي كمپرسورها در نظر گرفته شود. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
6 | در صفحه 98، Tag No. نهايي گردد. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
7 | تمامي Tag No. در نظر گرفته شود. براي مثال صفحه 97. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
8 | ارتباط سيستم ESD و F&G با سيستم كنترل در نظر گرفته شود. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
9 | در خصوص سيگنال هاي مربوط به Dehydration Pkg شفاف سازي صورت پذيرد. ارتباط با سيستم كنترل مركزي در نظر گرفته شود. |  | BK-SUR-ENG-INS-01-05365 | 2022-08-06 | اصلاح شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 6 Aug 2022 |  |  |  |  | Date: